## Slide 5
kb_per_day=-0.3, kw_per_day=0.0,
bulk_order=0, wall_order=0, duration_hours=72
Water age = average residence time of the mixed water body at the current node

## Slide 6
The first time, I randomly selected 20% of the old pipes and found little change.

## Slide 7
To make the change more apparent, the result can be obtained through subsequent inversion, so I fixed the position of the old pipe.

## Slide 11
During inversion, monitoring points can be weighted according to wall sensitivity.
Points that are too close to the tank or dominated by bulk (such as Node 20) are not suitable, otherwise during kw calibration, they will be driven by kb/tank.
Last week, there was a mistake: the node with the lowest average residual chlorine in node20 is not the point most sensitive to kw. It is greatly influenced by tank. The main source of change is kb.