## Slide 1
Week 1-2
Report
Ruixin Peng
June 1, 2026

## Slide 2
Ruixin Peng
June 2, 2026
1. WNTR Chlorine Modelling - Prep Work
2. Learning exercises
3. Material reading
4. My own understanding
Contents

## Slide 3
kb = -0.5/day, kw = -0.1m/day ??
near-source nodes (node 60 ≈ 1.0, node 10 ≈ 0.95) show almost no decay
far / branch nodes (nodes 15, 20, 40) fall much lower
There is a warm-up transient at the start (pipes/tanks filling from their initial state) before the system reaches a quasi-steady state -- so this initial period should be discarded when computing metrics later.
In my own paper, do I need to, eg. run for 72 hours and discard the first 24 hours?
Notes: 近的decay小，远的decay多。 单位是不是错了？ 初始设置只有reservoir是1，其他都是0，有warm-up。我自己的要不要warm-up？但是实际上，输入的是确定的，可能不用？

## Slide 4
Most kw-sensitive monitor (lowest mean residual): node 20
The more negative kw is, the lower the residual, and the curves spread out clearly into separate lines → here kw has a strong effect and is identifiable.
Notes: 可识别的

## Slide 5
Network map coloured by final chlorine
Residual chlorine exhibits a spatial gradient: highest near the source/reservoir and gradually decreasing along the distribution network toward the ends; lowest at ends, long branch pipes, and areas far from the source (most prone to problems).
The range of chlorine mentioned is (a, b) -- should we consider whether it exceeds b?
Actual vs measured
Notes: 氯的区间，考虑了下线，是否考虑上限。因为不会变多，只要输入的ok就行，但是测量的不一定。

## Slide 6
1. Bulk vs wall. Re-run with kw = 0. How much of Net's residual loss is bulk vs wall?
name | bulk-only (mg/L) | bulk+wall (mg/L) | loss_bulk (%) | loss_wall (%)
10 | 0.956 | 0.955 | 4.400 | 0.0
15 | 0.619 | 0.470 | 38.100 | 14.9
20 | 0.482 | 0.440 | 51.800 | 4.1
35 | 0.815 | 0.727 | 18.500 | 8.8
40 | 0.629 | 0.541 | 37.100 | 8.8
60 | 0.999 | 0.997 | 0.100 | 0.1
• The node with the highest absolute contribution from wall decay is node 15.
• The larger the loss_bulk, the "older" the water. Node 20 has the highest value (51.8%, longest water age), while node 60/10 has the lowest.
Wall decay contribution strongly depends on spatial location, pipe material and age (Hallam et al., 2002). Even with uniform kw values throughout the network, the proportion attributed to wall decay ranges from 0% to ~15% at different locations.
Division of labor with wall: at each point, bulk loss is ≥ wall, indicating that bulk is the dominant decay mechanism;
Notes: 这里主要是bulk
即使在整个管网中 kw 值保持一致，不同位置所归因于壁面衰减的比例也从 0% 到约 15% 不等

## Slide 7
Results: The four normalized curves perfectly overlap.
First-order kinetics dC/dt = -k·C is homogeneous/linear with respect to concentration.
2. Change INLET_CHLORINE_MGL and confirm residuals scale linearly. Why does that matter for treating the inlet monitor as a boundary condition?
This provides the justification for treating the DMA inlet monitoring point as a boundary condition -- simply inputting the measured inlet C(t) into the model is sufficient, without needing recalibration due to changes in absolute inlet levels.
Notes: 归一化，这为将DMA入口监测点作为边界条件提供了依据——只需将测得的入口C(t)输入模型即可，无需因入口绝对水平的变化而重新校准。

## Slide 8
3. Halve every pipe diameter. Wall decay should bite harder - why? (hydraulic radius / mass transfer; EPANET manual Ch.3).
Results:
Node 20/40 concentration is close to or equal to zero—these nodes did not receive any water at all
Node 15/35 concentration increased—the flow path was reconfigured, and water bypassed the tank
The curve is highly irregular, with "breakpoints" and "jumps," indicating the network is in a hydraulically infeasible state
wall reaction--4/d*kw(EPANET manual), kw1*kf/[rh(kw+kf)] (Vasconcelos et al., 1997)
Notes: 考虑水质和水力
回答他的问题，在wall里面，考虑了mass transfer, d也在公式里面

## Slide 9
Results: Near-source nodes (10/60) closely follow the inlet pattern, but distant nodes (20/40) experience stronger fluctuations instead.
The downstream residual chlorine curve is not simply a delayed or slightly reduced version of the inlet curve.
The water travel time in pipelines varies, and in storage tanks, new and old water mix, which alters the shape of the curve.
Therefore, it is essential to simulate the entire process using an EPANET/WNTR model.
During calibration, only a few steady-state points should not be used; instead, the full time series must be applied.
4. Use wn.add_source() with a pattern to make the inlet vary over time, mimicking a real inlet-monitor trace. This is exactly the boundary you'll impose later.
Notes: 下游余氯曲线不是入口曲线简单地“晚一点出现”或者“整体变小一点”。
水在管道里走的时间会变，水箱里还会混合新水和旧水，所以曲线形状会被改变。
因此必须用 EPANET/WNTR 模型来模拟整个过程。
校准时也不能只用某几个稳态点，而应该用完整时间序列。

## Slide 10
• Results:
The optimal grid point is (kb = -0.375, kw = -0.225), close but not equal to the true value (limited by the 9×9 coarse grid).
There are two grid points whose SSE falls within 1.5 times the minimum value: (-0.375, -0.22) and (-0.50, -0.22) -- their kw values are nearly identical (≥-0.22, close to the true value), while kb ranges from -0.375 to -0.50, all yielding "similarly good" fits.
5. Loop simulate_chlorine() over a (kb, kw) grid and compute the sum of squared errors (SSE) against a synthetic "observed" run.
kb-kw compensation: downstream residual chlorine only observes "total decay," so bulk and wall effects can compensate each other (a slightly higher kb and lower kw yield equally good fits).
Notes: 不同的kb和kw，可能得到相同的结果
获得的是一个Yield，存在kb-kw compensation补偿

## Slide 11
Paper | Key takeaway
A1 Rossman 1994 | first-order bulk + wall + mass-transfer = the EPANET model I will use
A6 Vasconcelos 1997 | kw ∝ 1/roughness; absolute error: 0.05-0.15 mg/L (my accuracy benchmark); fix kb from bottle tests, calibrate kw; DPD: 15% Process: (Hydraulic calibration), Bulk-bottle test, Adjust kw, Evaluation
A4 Hallam 2002 | wall decay is heterogeneous by material/age → justifies one kw per DMA
A3 Powell 2000 | bulk decay is driven by TOC/temperature → informs the kb prior
B1 Klise 2017 (WNTR) | EPANET wrapper + NetworkX + Pandas + built-in Monte Carlo
B2 EPANET 2.2 Manual | water-quality numerics: bulk/wall/mass-transfer term, unit conventions

## Slide 12
3 DMA points:
1. Hydraulic parameters are assumed correct without calibration.
2. TOC, DBP, and biofilm effects are not considered?
3. The inlet monitor has already measured it -- direct input (getting started -- normalization).
4. Attenuation: kw, kb, first-order attenuation
Based on prior experience, knowing the ranges of kb and kw, simulate a series of (kb, kw) pairs, compare Csim with Cobs to determine suitable Csim values and the corresponding interval for (kb, kw), and also obtain probabilities within reasonable ranges -- Monte Carlo ensemble, GLUE (Bayesian method not yet reviewed, uncertainty remains).
Monitoring point (3 inputs + 5 fittings + 2 validations)
?
Does kb share across DMA(same source?)? Does kb require separate calibration (jar test)?
Fix kb, calibrate kw or calibrate kb and kw simultaneously (in my opinion, more difficult).
Temperature?
Three DMAs (ABC), differing in pipe material and age (Hallam, 2002), were compared to determine whether a model calibrated on one DMA can be applied to another. (Using results from A to predict B and C, but I noticed the paper states they are not shared, so I believe prediction is not possible.)
My understanding
Notes: 现在大概的思路是：
我拿到3个DMA
1. 明确水力不用校准，默认正确
2. 不考虑TOC, DBP, 生物膜的影响？
3. 入口监测器已经把它测出来了，直接输入（getting started-归一性）
4. 衰减：kw, kb, 一阶衰减
根据先验经验，知道kb, kw范围，然后simulate，试出来一系列(kb, kw), 把Csim和Cobs比较，得出合适的Csim和合适的(kb, kw)的区间，也能得出在合理范围内的概率-Monte Carlo ensemble, GLUE(贝叶斯还没看不确定)
监测点（3输入+5拟合+2校验）
三个DMA（ABC），differ in pipe material and age（Hallam, 2002），得出的结论可比较
问
DMA是否同源-kb是否相同，kb是否需要单独校准
kb固定，校准kw or kb, kw同时校准（个人感觉更难）
温度
三个DMA（ABC），differ in pipe material and age（Hallam, 2002），得出的结论比较 or 在一个DMA上校准的模型能否适用于另一个DMA？(用A的结果预测B,C，但是我看到论文里说，不共用，所以我感觉不能预测)