# Identifiability, Prediction and Decision Robustness in Grouped Chlorine Wall-Decay Calibration: A Controlled EPANET Net3 Study

Ruixin Peng

August 2026

Programme: MSc [PROGRAMME — to confirm], Department of Civil and Environmental Engineering, Imperial College London

CID: [CID — to confirm] Supervisor: [FIRST SUPERVISOR — to confirm]

Module: CIVE70058 Research Paper

# Abstract

Grouped wall-decay coefficients are routinely calibrated from a handful of chlorine monitors, but the uncertainty reported can reflect the inference rule as much as the data, and whether parameter error reaches prediction or operational decisions is seldom tested. This study separates these effects in a controlled EPANET Net3 experiment with three synthetic reaction zones, known coefficients and six monitors. A censored Gaussian likelihood is compared with the informal weighting previously applied to the same system on identical observations and candidate draws; identifiability is triangulated across prior contraction, displaced priors, Fisher information, profile likelihood and repeated-noise calibration; and measurement, nuisance and structural errors are placed on common scales before propagation to prediction and low-chlorine risk.

Under known bulk decay and unbiased sensors, the formal rule contracted all three coefficients to 25–31% of their prior standard deviation, whereas the informal score at its original 0.120 mg L-1 behavioural threshold retained 86–98%. Both rules used the same 294 observations, so the difference is produced by the weighting alone. Treating bulk decay and monitor offsets as jointly unknown withdrew practical identifiability from the average and new coefficients. Recalibration over 100 noise realisations gave spreads closely matching the Cramér–Rao bound, at near-nominal 90% coverage. Systematic sensor error, bulk-decay misspecification and length-structured heterogeneity displaced coefficients by as much as 5.94 baseline posterior standard deviations, while the best achievable aggregate residual never exceeded the realised observation-noise RMSE by more than 6.2%. Yet when the old or average zone was withheld its coefficient returned to the prior midpoint and retained essentially the whole prior width, while held-out prediction at the omitted monitors stayed close to the 0.1 mg L-1 observation-noise scale. Displacements of several standard deviations largely preserved whole-network rank order, but they altered the six-node operational shortlist under one risk metric and not another.

Parameter identification, predictive adequacy and decision stability therefore require separate validation. All conclusions are bounded by a synthetic known-truth design with internal hold-out evaluation and no field data.

# 1. Introduction

## 1.1 Chlorine residual modelling as an inverse problem

A chlorine residual is maintained through a distribution network to provide continuing disinfection after treatment, and its concentration at any location reflects reaction in the bulk water, reaction at the pipe wall, and the transport and residence time that determine exposure to both (Rossman, Clark & Grayman, 1994; Vasconcelos et al., 1997). In the first-order representation implemented in EPANET, bulk decay is described by a coefficient kb in day-1 and wall decay by kw in m day-1, the wall reaction coupled to mass transfer from the bulk so that diameter and flow regime also affect its effective contribution (Rossman, 2000).

The two components are not equally accessible to measurement. Bulk decay can be estimated independently from controlled bottle tests, whereas wall decay is less directly observable. It depends on pipe-surface condition, corrosion products, deposits and biofilm, and generally has to be inferred from pipe-loop or field concentration data after accounting for bulk decay (Powell et al., 2000; Hallam et al., 2002). Because networks contain far more pipes than monitors, wall coefficients are commonly estimated for groups of pipes rather than individually, with grouping based on whatever physical or spatial information is available (Munavalli & Mohan Kumar, 2003; Nejjari et al., 2014).

Chlorine calibration is therefore an inverse problem rather than a curve-fitting exercise, and the distinction matters because the coefficients are not the only quantity of interest. Calibrated models are also used to predict concentrations at unmonitored locations, to identify areas susceptible to low residuals, and to support monitoring or control decisions. A calibration may therefore fail at several distinct levels. It may recover its parameters poorly, predict poorly, or give an unstable operational prioritisation, and these failures need not occur together.

## 1.2 Uncertainty, identifiability and their propagation

Several uncertainty sources act on such a problem. Random measurement noise and temporal dependence reduce the effective information in monitored series. Systematic sensor offsets or drift can bias inferred parameters while remaining difficult to diagnose from fit quality. Readings at a reporting boundary are censored rather than exact. Bulk decay is often estimated separately and then held fixed during wall-decay calibration, so an error in it can be absorbed by the wall coefficients. And any grouped representation is an approximation when reactivity varies between individual pipes. A close fit to monitored concentrations therefore does not by itself establish that the inferred coefficients represent the underlying reaction process.

Identifiability analysis addresses how strongly the observations constrain those parameters. Local sensitivity-based diagnostics examine whether nearby parameter changes produce distinguishable changes in the monitored outputs, which Fisher information and the associated Cramér–Rao bounds quantify under an assumed observation model (Brun, Reichert & Künsch, 2001). Practical identifiability additionally concerns whether the finite, noisy observations actually available constrain the parameters sufficiently, for which profile likelihood gives a direct likelihood-based diagnostic (Raue et al., 2009); repeated-sampling experiments can then test whether the resulting intervals show the bias and coverage the assumed model implies. No single diagnostic suffices. A posterior mean close to the truth may simply reflect favourable prior placement, and a narrow posterior may reflect a restrictive prior or a misspecified likelihood rather than physical correctness.

Uncertainty surviving calibration must finally be propagated to whatever decision the model supports, where stability is again not a single property: preservation of the whole-network spatial ranking, of a small operational shortlist, and of the absolute severity assigned to those locations are different questions, and stability at one scale does not imply stability at another.

## 1.3 Methodological gap

Three methodological questions motivate this study. First, conclusions about parameter uncertainty can depend on the inference formulation itself. GLUE-type environmental analyses may combine behavioural thresholds with informal likelihood measures whose statistical interpretation depends on their relationship to the assumed error process (Beven & Binley, 1992), and critiques have shown that a measure not representing the sampling distribution of model errors need not deliver formally calibrated parameter or prediction uncertainty (Mantovan & Todini, 2006; Stedinger et al., 2008). The controlled setting used here sidesteps that broader debate rather than resolving it. Because the synthetic observation model is known, the specific informal weighting previously applied to this system can be compared directly with the corresponding formal likelihood on identical observations and candidate draws.

Second, an identifiability result obtained under a favourable baseline does not establish that the same parameters remain recoverable once further uncertainty sources are admitted. Measurement precision, temporal dependence, systematic sensor error, bulk-decay uncertainty and within-group heterogeneity act in different ways, so loss of precision has to be separated from displacement of the estimate and both placed on a common scale.

Third, parameter identification, predictive adequacy and decision robustness answer different questions. A held-out prediction error cannot establish that the parameter governing a physical process has been identified, and a high whole-network rank correlation cannot establish that a small hot-spot set is unchanged.

## 1.4 Aim, research questions and scope

This study investigates how inference formulation and measurement, nuisance and structural-error assumptions affect the practical identifiability of grouped chlorine wall-decay coefficients, and whether the resulting parameter errors propagate to spatial prediction and to operational low-chlorine risk prioritisation. A synthetic experiment on the EPANET Net3 network is used so that the true coefficients are known, individual error sources can be introduced under controlled conditions, and every diagnostic can be evaluated against a known reference.

RQ1. Under the controlled baseline assumptions, how much information do six monitored chlorine series contain about three grouped wall-decay coefficients, and how strongly does the answer depend on the inference formulation?

RQ2. How robust is baseline parameter identification to random measurement error, temporal correlation, systematic sensor error, bulk-decay misspecification, zero-floor censoring and within-zone structural heterogeneity?

RQ3. Do errors in the inferred parameters necessarily degrade spatial prediction or operational prioritisation, and how does the answer depend on the risk metric used?

The study makes four contributions: a controlled comparison of a formal censored Gaussian likelihood against the specific informal weighting previously applied to this system, on identical observations and candidate draws; an identifiability assessment triangulated across posterior contraction, displaced priors, Fisher information, continuous profile likelihood and repeated-noise calibration; a separation of precision loss from parameter displacement across measurement, nuisance and structural perturbations on common reference scales; and an explicit distinction between parameter identification, predictive adequacy and decision robustness.

The scope is deliberately bounded. Network, zoning and truths are synthetic, the hydraulic model is treated as known rather than calibrated, chemistry is first-order in both bulk and wall reactions, and no field observations enter the analysis.

# 2. Method and approach

## 2.1 Study framework and controlled Net3 system

### 2.1.1 Network and hydraulic model

All experiments used the EPANET Net3 example network (Rossman et al., 2020) through WNTR (Klise et al., 2017), comprising 92 junctions, 117 pipes, three tanks, two reservoirs and two pumps. Hydraulic and reporting timesteps were 1 h and the water-quality timestep was 5 min. The hydraulic model was treated as known rather than calibrated: demands, pipe roughness, tank characteristics and pump controls were held at the values encoded in the frozen Net3 input file throughout, so the experiments below vary water-quality parameters or the observation process while retaining the same hydraulic representation.

### 2.1.2 Synthetic three-zone wall-decay representation

The pipes were divided into three synthetic spatial reaction zones by a deterministic rule on node coordinates. Nodes with y≤10 were assigned to the average zone; among the remainder, those with x≤26 were assigned to the new zone and those with x>26 to the old zone. A pipe whose end nodes fell in different zones was assigned to the weaker-reactivity side, under the fixed ordering new, average, old. This produced 14 old-zone, 37 average-zone and 66 new-zone pipes.

These labels denote synthetic reaction groups only. Net3 carries no pipe material or age information used by this study, so “old”, “average” and “new” should not be read as observed asset-condition classes.

Both bulk and wall reactions were represented as first-order processes. The synthetic truth assigned uniform wall-decay coefficients of −1.0, −0.1 and −0.05 m day-1 to the old, average and new zones. The baseline bulk-decay coefficient was fixed at −0.5 day-1, except in the robustness analyses of Section 2.5.5. Source chlorine was 1.0 mg L-1 and the tanks were initialised at 0.5 mg L-1.

### 2.1.3 Monitoring configuration and priors

Six junctions were used as calibration monitors, two in each synthetic zone: nodes 107 and 113 in the new zone, 15 and 145 in the old, and 209 and 231 in the average. This configuration also permits two distinct held-out designs to be separated: leave-one-monitor-out retains one local monitor in the withheld monitor’s zone, whereas leave-one-zone-out removes both.

The 48 h assessment window defined in Section 2.2.2 contains 49 hourly reporting points per monitor, giving 6×49=294 observations in the baseline calibration. Independent uniform priors were specified as [−1.5, −0.2], [−0.2, −0.04] and [−0.10, −0.005] m day-1 for the old, average and new coefficients. All three contain their synthetic truths but are not centred on them, which matters for interpreting any posterior that reverts towards its prior. Table 1 summarises the baseline design.

| Quantity | Old zone | Average zone | New zone | Unit |
| --- | --- | --- | --- | --- |
| Pipes | 14 | 37 | 66 | — |
| True wall decay | -1.000 | -0.100 | -0.050 | m/day |
| Prior range | [-1.500, -0.200] | [-0.200, -0.040] | [-0.100, -0.005] | m/day |
| Prior SD | 0.3753 | 0.0462 | 0.0274 | m/day |
| Monitors | 15, 145 | 209, 231 | 107, 113 | junction ID |

| Shared setting | Value |
| --- | --- |
| Bulk decay (first order, fixed) | -0.5 1/day |
| Source chlorine | 1.0 mg/L |
| Tank initial chlorine | 0.5 mg/L |
| Hydraulic and reporting timestep | 1 h |
| Water-quality timestep | 5 min |
| Total duration / warm-up / assessment window | 168 / 120 / 48 h |
| Observation error SD | 0.10 mg/L |
| Operational threshold | 0.20 mg/L |
| Candidate library | 8192 scrambled Sobol draws |
| Observations | 294 (6 monitors x 49 hourly values) |

Table 1. Baseline design and parameter ranges. Constants are held fixed across all experiments except where a later section states otherwise. Prior standard deviations are those of the uniform priors.

## 2.2 Forward simulation and synthetic observation generation

### 2.2.1 Forward chlorine simulation

The baseline synthetic truth was generated by running the EPANET water-quality model with the true zonal wall-decay coefficients, the fixed bulk-decay coefficient and the boundary concentrations of Section 2.1, storing concentrations at all 92 junctions including the six calibration monitors. This simulation defines the reference chlorine field from which the baseline observations are generated and against which baseline parameter and prediction recovery are evaluated; the robustness experiments of Sections 2.5 and 2.6 perturb either this field or its observation model explicitly.

### 2.2.2 Warm-up and assessment-window selection

Because storage makes the chlorine field settle slowly, warm-up was assessed by an explicit cyclostationarity test rather than chosen by convention. Demands and pump operation are 24 h periodic, so each cycle was compared with its successor against six diagnostics whose tolerances were declared in advance, evaluated at the synthetic truth and at both corners of the prior box.

The rule required every diagnostic to pass, and no cycle pair satisfied it within the 168 h model horizon. Because the inverse analyses depend directly on the chlorine field, 120 h was adopted instead, the earliest warm-up at which all three chlorine-concentration diagnostics passed. The assessment window is therefore 120–168 h, with 49 hourly reporting points per monitor. Definitions, tolerances and per-cycle values are in Appendix A; what the unmet diagnostics bound is reported in Section 3.1.2.

### 2.2.3 Synthetic measurement-error model

Synthetic observations were generated as

Cobs=max0,Ctrue+ϵ,ϵ∼N(0,σ2),

with a baseline σ=0.1 mg L-1. Throughout this study σ denotes one standard deviation of the assumed random measurement error, not a 95% interval or a hard error bound. The non-negativity floor means a latent reading below zero is recorded as zero; such observations are treated as left-censored in the primary likelihood rather than as exact zero measurements.

The reference observation set uses a fixed random seed. Repeated-noise experiments use separately generated realisations, whereas paired perturbation studies reuse identical noise seeds across comparison arms, so that a reported shift isolates the imposed perturbation rather than a change in the random draw.

### 2.2.4 Numerical and unit verification

All concentrations reported by the analysis are expressed in mg L-1, converted to WNTR’s internal kg m-3 representation on model input and back on output. The EPANET absolute quality tolerance was set to 1×10−5 mg L-1. This is a chosen setting rather than a unit conversion: it is a thousand times stricter than the EPANET default of 0.01 mg L-1, and holds the tolerance-to-source ratio fixed so that the corrected and superseded implementations can be compared as the same numerical experiment.

Three checks support the implementation. A single-pipe bulk-only configuration was compared with the analytic first-order solution C=C0exp(kbtres). Wall-reaction behaviour was checked for the expected sign, for monotonic response to the coefficient, and against the limiting case without mass-transfer resistance. A unit-equivalence test confirmed that the corrected implementation reproduces the previously generated field to within a maximum relative difference of 2.3×10−7, with no change in any of the below-threshold duration classifications tested. Agreement at this level is expected rather than fortuitous. First-order kinetics are invariant to the concentration scale, and every absolute quantity was rescaled together, including the source and tank concentrations, the observation standard deviation, the 0.2 mg L-1 threshold and the tolerance-to-source ratio, so the two implementations are the same numerical experiment. Any residual beyond solver tolerance would therefore have indicated a second, independent error. The Net3 input file is frozen and hash-checked, and the computational environment is pinned to exact library versions, which matters here because the study documents version-specific WNTR behaviour. The analysis code, the cached artifacts and these checks are archived in the project repository at the release cited in Appendix I. Full results are given in Appendix B.

## 2.3 Parameter sampling and inference formulations

### 2.3.1 Priors and Sobol candidate library

The three-dimensional baseline prior box was sampled with 8192=213 scrambled Sobol draws. Each baseline candidate was simulated once and its predictions at all 92 junctions cached. Experiments that changed only the observation realisation or the weighting rule reused this common library; in particular the censored Gaussian, iid Gaussian and informal GLUE formulations were evaluated on identical prior draws and identical model predictions, so any difference between those baseline inference results is attributable to the weighting formulation rather than to sampling or to different forward simulations. Experiments that altered the prior domain or a forward-model parameter generated their own prediction libraries under the same sampling principles. These were the displaced-prior tests of Section 2.4.2, the bulk-decay cases of Section 2.5.5 and the scenarios of Section 2.8.4.

Sampling convergence of the baseline weighted ensemble was assessed on the nested leading Sobol subsets of 1024, 2048, 4096 and 8192 candidates, comparing posterior medians, quantiles and effective sample size. The effective sample size, ESS=1/iwi2, is reported throughout as a diagnostic of how far the discrete weights concentrate.

### 2.3.2 Censored Gaussian likelihood

The primary inference rule was a censored Gaussian likelihood. Up to additive constants independent of the parameter vector θ,

ℓ(θ)=−12yi>0yi−μi(θ)σ2+yi=0logΦ−μi(θ)σ,

where yi is an observed concentration, μi(θ) the corresponding model prediction and Φ the standard-normal cumulative distribution function. Positive observations contribute Gaussian residual terms; observations recorded at the zero floor contribute the probability that the latent reading lies at or below that floor.

The rule uses the uniform priors of Section 2.1.3 and has no behavioural acceptance threshold. Because candidates are drawn directly from those priors, their normalised likelihood weights are a discrete Monte Carlo approximation to the posterior over the sampled space. Weights were computed in numerically stable form as

wi=expℓ(θi)−ℓmaxjexpℓ(θj)−ℓmax,

from which weighted means, standard deviations, quantiles and effective sample sizes follow.

### 2.3.3 Formal iid Gaussian comparator

A formal iid comparator used the same prior draws, the same observation-error standard deviation and the same Gaussian residual model, but treated every recorded value as exact, including those at the zero floor. It therefore differs from the primary rule only in its handling of censored readings, and exists solely to quantify what that handling contributes; it is not a second primary analysis.

### 2.3.4 Informal GLUE behavioural comparator

The specific informal GLUE weighting used in the original analysis of this system was retained as a comparator, so that its effect could be measured on the same observations and predictions as the formal rules. Candidate i received weight

wiGLUE∝exp−12RMSEiσ21RMSEi<T,

with T a behavioural RMSE threshold. Three thresholds were examined: 0.107, 0.110 and 0.120 mg L-1. The first is the approximate one-sided 95% upper acceptance band of the RMSE objective evaluated at the truth,

T(σ)=σ1+z2N,

which for z=1.645, N=294 and σ=0.1 mg L-1 gives 0.1068 mg L-1. This is a statement about the sampling distribution of the objective at the truth, not a credible interval for the parameters. The 0.120 mg L-1 threshold reproduces the original analysis and 0.110 provides an intermediate case. Threshold sensitivity is a property of this comparator alone; neither formal rule uses an acceptance threshold.

## 2.4 Identifiability analysis

### 2.4.1 Prior contraction

Posterior contraction was summarised by the retained-standard-deviation ratio RSD,j=σpost,j/σprior,j, reported throughout as SD retained. A value near one indicates little reduction in prior dispersion; smaller values indicate stronger contraction. Posterior means are reported alongside it because contraction and truth recovery are distinct: a mean close to the synthetic truth is weak evidence when the prior is already favourably placed, and a narrow posterior can still be displaced under model or observation error. SD retention is therefore treated as a contraction diagnostic, not as a sufficient identifiability test on its own, which is why the four further analyses below are needed.

### 2.4.2 Displaced-prior tests

To separate information supplied by the observations from favourable prior placement, the calibration was repeated over 30 independent noise realisations using displaced prior boxes of unchanged width. In the DOWN design each box retained its original width but was re-centred at the known synthetic truth minus one original-prior standard deviation, so the displacement is defined relative to the truth rather than to the original midpoint. In the OLDUP design only the old-zone box changed direction, being centred at the truth plus one original-prior standard deviation, while the average and new boxes kept their DOWN positions; OLDUP is therefore a directional check for the old coefficient rather than a second like-for-like three-parameter test. An upper cap of −0.005 m day-1, imposed to keep the old prior in the non-positive decay domain, then shifted that box down to a realised midpoint of −0.655 m day-1, about 0.92 original-prior standard deviations from the truth rather than the intended one.

Recovery was measured as the fraction of the imposed displacement closed,

Gj=μpost,j−mdisp,jktrue,j−mdisp,j,

where mdisp,j is the displaced midpoint. Gj=0 means the estimate stays at that midpoint, Gj=1 means full recovery to the truth, and values above one mean movement beyond it.

### 2.4.3 Fisher information and Cramér–Rao bounds

Local identifiability was assessed from the sensitivity Jacobian of the 294 monitored values. For independent homoscedastic Gaussian errors,

F=1σ2JTJ,Jij=∂Ci∂θj.

evaluated at the synthetic truth by finite differences. The calculation assumes errors at σ=0.1 mg L-1 and does not include the censoring correction, so it is a local information benchmark rather than a duplicate of the primary likelihood.

Three nested parameterisations were examined: (A) the three wall-decay coefficients alone; (B) those plus bulk decay; and (C) those plus bulk decay and six monitor-specific offsets, each constant across that monitor’s 49 observations. In B and C the nuisance parameters were marginalised and the marginal Cramér–Rao standard deviations normalised by the corresponding prior standard deviation, a ratio below one being the criterion for local practical identifiability adopted here. This is a benchmark relative to the chosen prior scale, not a universal threshold. Marginalisation and the step-size check are in Appendix D.

### 2.4.4 Continuous profile likelihood

Likelihood geometry was assessed by continuous single-parameter profiles: each wall coefficient was fixed in turn while the other two were re-optimised by Nelder–Mead within their prior bounds, and the endpoints of the 95% interval were located by Brent bisection at

ΔNLL≤12χ1,0.952≈1.92.

Profiles were computed under the primary censored likelihood, with an iid Gaussian profile retained as a censoring benchmark. A 21-point-per-parameter grid was kept for visualisation only, because a discrete grid can place interval endpoints only at its nodes.

### 2.4.5 Repeated-noise calibration

Repeated-sampling behaviour was assessed by recalibrating for 100 independent observation-noise realisations. For each coefficient the analysis recorded the bias of the posterior mean, the empirical standard deviation of that mean across realisations, its ratio to the Case-A Cramér–Rao bound, and the mean posterior standard deviation reported within individual realisations. The last of these asks whether the uncertainty a single calibration claims matches the estimator’s actual sampling spread. Empirical coverage was evaluated for nominal 90% and 95% weighted posterior-quantile intervals, with normal-approximation intervals as a secondary check.

The observation-error draws are independent, but all 100 calibrations are evaluated against the same 8192-member Sobol prediction library, so their finite-library Monte Carlo errors are correlated; the effective-sample-size distribution is reported as a numerical-resolution diagnostic.

## 2.5 Robustness to measurement and nuisance errors

Two kinds of effect are distinguished throughout, and reported on different scales. Widening is the loss of precision when an uncertainty source is represented in the inference; displacement is the movement of an estimate when a perturbation is imposed but not represented. For coefficient j the standardised displacement is

ZΔ,j=medianrμj,rpert−medianrμj,rrefmedianrσj,rref,

where the reference is the set of 30 unbiased realisations at σ=0.1 mg L-1. The denominator is thus the median within-realisation posterior standard deviation under the repeated unbiased baseline, not the single-realisation value of Section 3.2.

### 2.5.1 Random measurement error

Sensitivity was evaluated at σ=0.02, 0.05, 0.10 and 0.15 mg L-1 with 30 independently generated noise realisations at each level. The same σ was used both to generate the observations and in the corresponding likelihood, and the informal comparator used the σ-dependent threshold of Section 2.3.4.

Effective sample size distinguishes inferential change from inadequate numerical resolution. A row was flagged as sampling-limited when its median ESS fell below 100, or when any realisation produced an empty behavioural set; contraction from such rows is not interpreted as a quantitative estimate of the benefit of that sensor precision, because a sharper likelihood concentrates on a library drawn for the baseline noise level.

### 2.5.2 Temporal autocorrelation

Temporal dependence was treated as an assumed covariance sensitivity rather than an estimated property, since the baseline observations are generated independently. Each monitor’s 49 hourly residuals were assigned a first-order autoregressive covariance Σm(t,s)=σ2ρ|t−s|, with the six monitor blocks mutually independent, and the Fisher information recomputed as FAR1=JTΣ−1J rather than by a scalar effective-sample-size correction. The principal case used ρ=0.4, with a sweep over ρ=0, 0.2, 0.4, 0.6 and 0.8 reported in Appendix D.

### 2.5.3 Sensor bias and drift

Systematic error was added to the synthetic measurement before the non-negativity floor, Cobs=max0,Ctrue+ϵ+b, so that a negative offset pushes more readings onto the floor than a positive one of the same size. Offsets were applied at each of the six monitors, giving 24 bias arms of 30 noise realisations each; only the observations are perturbed, so candidate predictions are unchanged.

Drift was examined at monitors 15 and 231 as a linear ramp b(t)=D(t−t0)/48 over the window, correct at the start and off by D at the end, paired under identical noise with constant-offset controls at its mean and endpoint values. This separates the drift’s temporal shape from its mean magnitude. Offsets, arm definitions and per-arm results are in Appendix F.

### 2.5.4 Zero-floor censoring

The primary censored likelihood and the formal iid exact-zero comparator were applied to the same synthetic observation sets over 30 noise realisations, so that only the statistical treatment of readings recorded at zero changed while the observations and predictions stayed identical. The number of floored readings and the resulting risk ranking were recorded alongside the coefficient difference.

### 2.5.5 Bulk-decay misspecification

Observations were generated at the true kb=−0.5 day-1 and the wall coefficients recalibrated with kb fixed at −0.4 and −0.6 day-1, that is ±20% misspecification, over the same 30 noise realisations. Besides parameter displacement, the resulting risk fields were compared under both the duration-based P=E[D]/48 and the cumulative-deficit E[A] rankings defined in Section 2.8.1.

## 2.6 Structural heterogeneity experiments

Headline structural effects use the primary censored likelihood; the length-structured experiment was additionally run with the informal GLUE comparator, to test whether the inference formulation alters the apparent response to structural misspecification.

### 2.6.1 Symmetric within-zone heterogeneity

Unstructured heterogeneity was generated as kw,p=kw,z(1+δp) with δp∼U(−J,J) and J=0, 0.20, 0.35 or 0.50. The perturbation distribution is symmetric about the nominal zone coefficient, but a finite random field need not have exactly zero sample mean, so coefficient error is evaluated against each realised field’s own arithmetic zone mean rather than the nominal value.

The zero-jitter arm is a homogeneous paired control. The same underlying random variates and the same noise realisation were reused across the magnitude sweep, so differences between arms reflect heterogeneity magnitude rather than a different spatial arrangement or noise draw. Because one spatial realisation cannot establish a systematic effect, the J=0.20 case was repeated over 25 independently generated pipe-level fields with the noise realisation held fixed, so that the resulting between-field scatter isolates sensitivity to the arrangement itself.

### 2.6.2 Length-structured within-zone heterogeneity

The second experiment introduced deterministic structure while keeping the same three zones. Within each zone, pipes were ranked by length and given a centred rank score sp∈[−1,1] rising from the shortest to the longest pipe and having zero mean, and the pipe coefficient was set to

kw,p=kw,z1+λsp.

Since kw,z<0, a larger sp makes the coefficient more negative, so longer pipes decay more strongly. The zero mean of sp holds each zone’s arithmetic coefficient exactly at kw,z while its length-weighted mean shifts towards stronger decay, which is what makes the two candidate targets distinguishable.

The length-structure amplitude was varied over λ=0, 0.25, 0.50 and 0.75. λ is a modulation amplitude, not a Pearson or Spearman correlation coefficient: the length ranking and the coefficient ranking are perfectly monotone for any λ>0, and λ sets only how far the coefficients spread about the zone mean. At λ=0 the truth is homogeneous and the two target means coincide. Each non-zero amplitude used 30 independent noise realisations. Only the truth is heterogeneous; calibration retains the three-zone homogeneous model with one fitted coefficient per zone.

### 2.6.3 Structural-effect metrics

Structural effects were summarised by the four quantities Table 2 defines, because they answer different questions. Raw bias measures the fitted coefficient against the realised arithmetic zone mean; the paired structural increment removes the offset the same rule produces on a homogeneous truth under the same noise; the standardised displacement puts that paired shift on the scale of Section 2.5 using the repeated-baseline denominator; and the displacement fraction locates the fit between the arithmetic and length-weighted references, reported raw rather than control-adjusted. Full definitions and per-design results are in Appendix E.

## 2.7 Internal prediction validation

Four complementary validation designs were used to separate predictive performance from parameter identification. Leave-one-monitor-out withheld each of the six monitors in turn while retaining the second monitor of that zone; leave-one-zone-out withheld both monitors of a zone, removing all direct observation of it. Both were repeated over 30 independent noise realisations.

The two designs predict a noisy held-out observation, so their 90% predictive intervals combine ensemble and observation variance, C±1.645Varw[C]+σ2. They report held-out RMSE and empirical coverage; leave-one-zone-out additionally reports the withheld zone’s coefficient error and SD retained.

A separate spatial validation calibrated on all six monitors and predicted at 20 junctions that never entered any calibration, scored against the noise-free truth and summarised by coverage and by the normalised mean absolute error, NMAE=t|Ct−Ct|/t|Ct|, evaluated per junction over the assessment window. This normalises by the mean of the truth rather than averaging pointwise ratios, which would be unstable where the true concentration approaches zero. Its bands therefore carry ensemble parameter uncertainty only, without the σ2 term. Finally, leave-one-zone-out was repeated under ±20% within-zone heterogeneity across eight independently generated fields, each with its own noise draw, with coefficient error measured against that field’s own arithmetic zone mean.

## 2.8 Operational risk assessment

### 2.8.1 Low-chlorine metrics

The likelihood-weighted ensemble was propagated to all 92 junctions and evaluated against Ccrit=0.2 mg L-1, a representative operational threshold adopted for this study rather than a regulatory limit. Five member-level quantities and their weighted summaries are defined in Table 2. They are kept distinct because a window-breach probability, a time-averaged breach probability, an expected duration, a cumulative deficit and a window minimum describe different aspects of low-chlorine behaviour: the first records only whether a threshold was crossed, whereas the deficit combines how long and how far. Duration and deficit were integrated by trapezoid over the 48 one-hour intervals, and the per-member minimum was summarised by weighted means and quantiles rather than reported as a single deterministic value. The weights propagated here are those of the baseline calibration, which was conditioned on one reference observation realisation. Every risk figure quoted below is therefore conditional on that realisation and is not a median over the 30 noise realisations used for the inference diagnostics; observation-noise variability enters the risk results only through the perturbation comparisons of Section 3.6.2.

### 2.8.2 Water age and demand weighting

Water age was computed over the same window as a reaction-independent diagnostic, and its spatial association with expected duration and cumulative deficit described by Spearman rank correlation. The 92 junctions are not independent samples, so no junction-level p-value is reported; for the duration association a descriptive width was obtained by resampling whole spatial blocks, with the design in Appendix G. Network summaries were reported over all 92 junctions, over the 59 with non-zero demand, and demand-weighted, because the three answer different questions.

### 2.8.3 Ranking robustness

Robustness was assessed at two scales that are not interchangeable. The primary network-scale statistic is the Spearman rank correlation between perturbed and reference risk fields across all 92 junctions; the primary shortlist statistic is the top-six Jaccard index (Table 2), six being the common headline size. Kendall correlation and alternative shortlist sizes were retained as supplementary diagnostics where computed. For perturbations repeated over noise realisations, nodewise risk values were first reduced to their median across realisations and the ranking statistics computed from that median field. Both statistics were evaluated separately under the duration-based and deficit-based metrics, since the two need not identify the same leading junctions.

### 2.8.4 Temperature, ageing and dosing scenarios

The ensemble was propagated through four scenarios using Arrhenius scaling,

k(T)=k(Tref)exp−EaR1TK−1Tref,K,

with Tref=12 °C. Activation energies and a temperature deviation added to each scenario mean were drawn from truncated normals keeping simulated temperatures inside the stated 8–24 °C validity range, with the distributions in Appendix G. The scenarios were: (A) 12 °C baseline; (B) 16 °C; (C) 20 °C heatwave; and (D) 20 °C with illustrative ageing multipliers of 1.00, 1.35 and 1.85 for the new, average and old zones.

Draws were reused across scenarios, so pairwise differences are not contaminated by Monte Carlo variation. Only candidates whose weight was at least 10−6 of the maximum weight were propagated, a numerical truncation rather than an acceptance threshold. Corrective dosing was evaluated under Scenario C, the heatwave without ageing, raising reservoir source chlorine from 1.00 to 1.15 and 1.30 mg L-1 with tank initial chlorine scaled by the same factor.

| Symbol | Definition | Section |
| --- | --- | --- |
| RSD,j | σpost,j/σprior,j, reported as SD retained | 2.4.1 |
| Gj | (μpost,j−mdisp,j)/(ktrue,j−mdisp,j), fraction of an imposed prior displacement recovered | 2.4.2 |
| ESS | 1/iwi2, effective sample size of the normalised weights | 2.3.1 |
| ZΔ,j | standardised displacement: median perturbed minus median reference posterior mean, divided by the median within-realisation reference posterior SD | 2.5 |
| Δkraw | k−karith, raw bias against the arithmetic zone mean | 2.6.3 |
| Δkstruct | Δkraw−Δkhom, bias net of the paired homogeneous control | 2.6.3 |
| fj | (kj−karith,j)/(klength,j−karith,j), raw position between the two candidate targets | 2.6.3 |
| λ | length-structure modulation amplitude in kw,p=kw,z(1+λsp); not a correlation coefficient | 2.6.2 |
| Di,n | ∫1[Ci,n(t)<Ccrit]dt, member duration below threshold | 2.8.1 |
| Ai,n | ∫max[0, Ccrit−Ci,n(t)]dt, member cumulative deficit | 2.8.1 |
| Mi,n | mintCi,n(t), member window minimum | 2.8.1 |
| E[Dn], E[An] | iwiDi,n and iwiAi,n, weighted expectations | 2.8.1 |
| Pn | E[Dn]/48, time-averaged below-threshold probability | 2.8.1 |
| Pmin,n | iwi1[Mi,n<Ccrit], probability of at least one breach in the window | 2.8.1 |
| Jk | ¦Skpert∩Skref¦/¦Skpert∪Skref¦, top-k shortlist overlap | 2.8.3 |

Table 2. Symbols and metric definitions. Integrals run over the 120–168 h assessment window and wi are the normalised likelihood weights of Section 2.3.2.

# 3. Results and discussion

## 3.1 Forward-model baseline and synthetic observations

### 3.1.1 Baseline chlorine dynamics across the monitored network

The baseline inverse problem is anchored to a single reference forward field, described here; Sections 3.3 and 3.4 perturb that field or its observation model explicitly. Under the imposed truth, concentrations across the assessment window follow the 24 h demand and pump cycle with a network-wide median of 0.761 mg L-1 and a 5th-to-95th percentile range of 0.168 to 0.956 mg L-1 (Figure 1B, C).

The six monitors sample most of that range rather than replicating one another. Mean window concentrations are 0.845 and 0.827 mg L-1 at nodes 107 and 113 in the new zone, 0.717 and 0.374 at nodes 209 and 231 in the average zone, and 0.251 and 0.355 at nodes 15 and 145 in the old zone. The broad zonal pattern follows the imposed reactivity contrast, but concentration is not ordered by wall-decay coefficient alone: node 231 in the average zone sits below node 145 in the old zone, because hydraulic residence and network position also strongly modulate the accumulated decay. In the deterministic noise-free reference trajectory, 21 of the 92 junctions cross below the 0.2 mg L-1 operational threshold at least once during the window; this is a property of the truth and is not the ensemble-weighted breach count reported in Section 3.6.

### 3.1.2 Warm-up and assessment-window adequacy

The three concentration criteria, at the monitors, in the network 95th percentile and in the tanks, were all first satisfied at 120 h, which is why the assessment window begins there.

Two criteria were never satisfied inside the model horizon. The 95th-percentile water age was still changing by 12.8 h between the last two available cycles, and the network-mean cumulative deficit by as much as 5.1%. The hotspot pattern moves with it. Over the same comparison the top-10 cumulative-deficit sets at the truth had a Jaccard overlap of 0.818, one node in ten differing. The horizon could not be extended without modifying the model (Appendix A). Parameter inference is therefore supported by a concentration-stable window, whereas absolute water ages, absolute risk severities and some hotspot boundaries in Section 3.6 retain a residual dependence on the horizon and are used for comparison between conditions rather than as calibrated magnitudes.

### 3.1.3 Signal and noise characteristics of the synthetic observations

Observations were formed by adding Gaussian noise with a standard deviation of 0.1 mg L-1 to the true series at the six monitors and flooring the result at zero, giving 6 x 49 = 294 residuals. The realised noise RMSE over the window was 0.0973 mg L-1, while the minimum RMSE anywhere in the 8192-member candidate library was 0.0971 mg L-1: the best candidate therefore fits the observations to approximately the imposed noise floor. This establishes that a low aggregate residual is attainable, not that the corresponding parameter vector is correctly identified. Small residual differences accumulated over 294 observations may still carry substantial inferential information, and Section 3.2 measures how much of it the competing weighting rules extract.

The same absolute error represents very different relative perturbations across the network: at node 107 a standard deviation of 0.1 mg L-1 is about 12% of the mean concentration, against roughly 40% at node 15. The low-concentration old-zone monitors therefore operate at a poorer concentration-scale signal-to-noise ratio, although parameter information ultimately depends on the concentration Jacobian rather than relative concentration alone (Section 3.2.3). In the reference realisation, ten of the 294 observations were floored at zero. Six of these were at node 15, three at node 145 and one at node 231, that is nine in the old zone and one in the average zone, none in the new zone. Censoring is thus concentrated in the part of the network most relevant to the threshold-based risk analysis that follows, and is handled explicitly in the primary likelihood.

Figure 1. Study system and forward baseline. (A) Net3 with pipes coloured by synthetic reaction zone. (B) True concentration at the monitors over the assessment window, with the noisy calibration observations. (C) Per-junction window minimum over the deterministic truth.

## 3.2 Inference formulation determines apparent identifiability

### 3.2.1 The same observations under three weighting rules

How much of any answer about parameter information is a property of the weighting rule rather than of the data? All three rules were applied to one library of 8192 candidates, so observations, prior and candidate set were identical and only the weighting changed.

The three rules disagree sharply (Table 3, Figure 2). Under the primary censored Gaussian likelihood the posterior standard deviation was 25.0%, 30.7% and 28.3% of the prior standard deviation for the old, average and new coefficients respectively. Under the informal GLUE score at the threshold used in the original analysis, RMSE < 0.120 mg L-1, the same 294 residuals left 85.8%, 98.4% and 98.0% of the prior standard deviation intact: the average and new behavioural distributions retained essentially the full prior dispersion and were effectively prior-dominated under this rule. The formal iid comparator, which differs from the primary rule only in treating a floored reading as an exact zero, returned 24.5%, 30.6% and 28.3%; the treatment of the ten floored observations therefore cannot explain the formal–informal difference in this experiment.

| Coefficient | Truth | Prior SD | Scheme | Mean | SD | SD retained | ESS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| old | -1.000 | 0.3753 | formal censored | -0.9876 | 0.0938 | 25.0% | 157 |
|  | -1.000 | 0.3753 | formal iid | -0.9708 | 0.0920 | 24.5% | 154 |
|  | -1.000 | 0.3753 | informal GLUE 0.107 | -1.0115 | 0.2668 | 71.1% | 4783 |
|  | -1.000 | 0.3753 | informal GLUE 0.120 | -0.9431 | 0.3220 | 85.8% | 7062 |
| average | -0.100 | 0.0462 | formal censored | -0.1091 | 0.0142 | 30.7% | 157 |
|  | -0.100 | 0.0462 | formal iid | -0.1087 | 0.0141 | 30.6% | 154 |
|  | -0.100 | 0.0462 | informal GLUE 0.107 | -0.1170 | 0.0424 | 91.8% | 4783 |
|  | -0.100 | 0.0462 | informal GLUE 0.120 | -0.1196 | 0.0455 | 98.4% | 7062 |
| new | -0.050 | 0.0274 | formal censored | -0.0440 | 0.0078 | 28.3% | 157 |
|  | -0.050 | 0.0274 | formal iid | -0.0441 | 0.0078 | 28.3% | 154 |
|  | -0.050 | 0.0274 | informal GLUE 0.107 | -0.0492 | 0.0242 | 88.2% | 4783 |
|  | -0.050 | 0.0274 | informal GLUE 0.120 | -0.0529 | 0.0269 | 98.0% | 7062 |

Table 3. Baseline inference comparison. Three weighting rules on the same 294 residuals and 8192 Sobol candidates, the informal score at both thresholds, for the reference noise realisation. SD retained is the weighted-ensemble standard deviation as a percentage of the prior; it is a posterior standard deviation only under the two formal rules, since the informal score is not a likelihood.

Figure 2. Inference formulation determines apparent identifiability. Weighted densities for the reference noise realisation under the uniform prior, the primary censored likelihood and the informal score at two thresholds, with dashed rules at the true values. Bars give the weighted-ensemble standard deviation as a percentage of the prior, which is a posterior standard deviation only under the two formal likelihoods.

The weights show why, and the reason is arithmetic. The formal weights concentrate on an effective sample of about 157 of 8192 draws (1.9%), whereas the informal effective sample size almost equalled the number of retained candidates, at 4783 of 4786 for a threshold of 0.107 and 7062 of 7084 at 0.120, so the weights were nearly uniform within the accepted set. For an iid Gaussian residual model the informal log-weight is the Gaussian log-likelihood divided by N, up to a constant: equivalently it weights residuals as though the standard deviation were σN=1.71 mg L-1 at N=294, seventeen times the assumed sensor noise and above the 1.0 mg L-1 source concentration.

This is consistent with published criticisms of informal likelihood measures, which do not accumulate information at the rate implied by the number of observations, so their distributions describe the analyst’s acceptance rule as much as the evidence (Mantovan & Todini, 2006; Stedinger et al., 2008). The point here is narrower than the general debate over generalised likelihood uncertainty estimation (Beven & Binley, 1992; Beven & Binley, 2014): it concerns the specific pseudo-likelihood implemented in the original analysis, not the behavioural philosophy. Because the two families differ by the weighting alone, the wide informal distributions cannot be read as evidence that six monitors are uninformative about three grouped coefficients. Whether the formal contraction is itself trustworthy is a separate question, taken up next.

### 3.2.2 Thresholds cannot substitute for the omitted information factor

Tightening the informal cut-off from 0.120 to 0.107 mg L-1 reduced the behavioural set from 7084 to 4786 candidates, yet the retained prior standard deviations fell only to 71.1%, 91.8% and 88.2%, still two to three times the formal values. Candidate rejection therefore cannot restore the information factor N the score omits.

To exclude favourable prior placement as the cause of the formal contraction, all three prior boxes were re-centred at the truth minus one original-prior standard deviation, keeping their original width, and the calibration repeated over 30 noise realisations. The formal likelihood recovered 88%, 95% and 96% of the imposed displacement for old, average and new while retaining 27.1%, 28.9% and 28.4% of the displaced prior’s standard deviation, matching the baseline contraction from a prior no longer centred on the truth. The informal comparator recovered substantially less at both thresholds.

The OLDUP check reversed the old-zone displacement alone. Because the non-positivity constraint shifted its realised midpoint to −0.655 m day-1, the upward displacement is about 0.92 original-prior standard deviations rather than a full one. Formal recovery for old was 88% downward and 112% upward, symmetric within the noise, whereas informal recovery moved strongly with the direction of displacement. The pronounced identifiability gradient reported in the original analysis, in which old appears far better constrained than average or new, is therefore a property of the weighting rule rather than a ranking of what the monitoring array can resolve. Full threshold and displacement matrices are given in Appendix C.

### 3.2.3 Three further diagnostics agree with the baseline result

Prior contraction under a single likelihood and a single noise realisation is weak evidence on its own, so the baseline was checked against three diagnostics that fail in different ways (Figure 3). The Cramér–Rao bound computed from the Fisher information for the three wall-decay coefficients alone gives standard deviations of 0.095, 0.014 and 0.008 m day-1, equivalent to 25.2%, 29.2% and 29.0% of the prior standard deviation and matching the ensemble result to within about 1.5 percentage points. Continuous profile likelihood intervals at the 95% level are [-1.172, -0.811], [-0.137, -0.082] and [-0.060, -0.029] m day-1, each covering its true value; endpoints obtained by bisection are quoted rather than grid endpoints, which understate the half-width by 39.0%, 14.9% and 28.1% and are used here only for visualisation. Finally, repeating the calibration over 100 independent noise realisations gave a mean bias of at most 0.15 times the empirical sampling standard deviation, a ratio of empirical spread to the Cramér–Rao bound of 1.04, 1.06 and 1.12, and 90% interval coverage of 0.89, 0.88 and 0.85, close to nominal, with the new coefficient slightly under-covered.

Figure 3. Three further diagnostics agree with the baseline result. Intervals from the likelihood-weighted ensemble (5–95%), continuous profile likelihood (95%), the Fisher bound (95%) and 100 repeated-noise calibrations (mean ± SD).

Their agreement is convergent evidence of practical identifiability under the controlled baseline, and each would fail differently were that result an artefact, being insensitive respectively to the sampling design, the prior, and the realisation that produced the baseline (Brun, Reichert & Künsch, 2001; Raue et al., 2009).

The conditions are strong: bulk decay fixed at its true value, sensors unbiased, errors independent and Gaussian with known standard deviation, and the three-zone grouping correctly specified. Two numerical caveats apply. The likelihood-weighted Sobol ensemble has an effective sample size of about 157, limiting the Monte Carlo resolution of its weighted moments and quantiles; the profile intervals are obtained independently of that library, but all 100 repeated-noise realisations reuse it, so their Monte Carlo errors are correlated.

## 3.3 Practical identifiability under measurement and nuisance errors

### 3.3.1 Random measurement error and temporal autocorrelation

Section 3.2 established what the six monitors resolve when every assumption holds; this section relaxes them one at a time. Figure 4 collects the comparison on two scales: widening for the two sources that only inflate uncertainty, displacement in baseline posterior standard deviations for the six that move the estimate.

A 50% rise in the assumed measurement error, from 0.10 to 0.15 mg L-1, degraded identifiability less than the original analysis implied: it widened the posterior by 1.41, 1.52 and 1.48 times, leaving 38.1%, 44.9% and 43.1% of the prior standard deviation. The claim that a precision of 0.05 mg L-1 was required therefore reflects the informal score’s inefficiency rather than a demonstrated sensor specification. At 0.10 mg L-1 it returned standard deviations 2.4 to 3.1 times the formal ones. The converse benefit cannot be quantified here: at 0.05 and 0.02 mg L-1 the sharper likelihood concentrates on a library not drawn for it, the median effective sample size falls to 21 and 2 draws, and those rows are reported as sampling-limited.

Temporal correlation is an assumed sensitivity, not an estimated property, since the observations are independent by construction. The usual scalar approximation would put the effective sample size at about 126 of 294 at a correlation of 0.4; recomputing the Fisher information from the full block covariance instead widened the three bounds by 1.48, 1.49 and 1.44 times, to 37.5%, 43.5% and 41.7% of the prior standard deviation. Correlation at this strength inflates uncertainty without removing information. The field-relevant case is the converse. Modelling correlation that is present widens the intervals, whereas fitting an independent-error likelihood to observations that are genuinely correlated would narrow them, reporting a precision the data do not support.

### 3.3.2 Systematic sensor error produces large coefficient displacement

Systematic error behaves differently. Constant offsets of +0.05 and +0.10 mg L-1 at node 15 alone moved the old-zone estimate by 2.19 and 3.87 baseline posterior standard deviations: with no sensor-offset parameter in the calibration, instrument error is absorbed into the wall coefficients rather than represented. The response is asymmetric in sign, because a downward bias pushes more readings onto the censoring floor. The same offsets applied negatively gave 2.59 and 3.82.

Sweeping the offset across all six monitors, 24 arms, shows the damage depends on where the biased sensor sits: the largest displacement for any coefficient in any arm was 3.87 standard deviations for old (node 15, +0.10 mg L-1), 5.94 for average (node 231, −0.10) and 4.44 for new (node 113, −0.10). Contamination crosses zone boundaries. A −0.10 offset at new-zone node 107 displaced the average coefficient by 1.59. Per-arm results are in Appendix F.

Drift is governed by its mean, not its endpoint. A ramp reaching a given offset by the end of the window displaced the estimate by 0.89 to 0.99 times a constant offset at half that value, but only 0.45 to 0.64 times one at the endpoint value: a sensor drifting to +0.10 mg L-1 behaves much more like a constant +0.05 than a constant +0.10. By comparison the censored readings are a small correction. Across 30 independent noise realisations, treating them as exact zeros rather than as left-censored moves the old coefficient by a median of 0.11 baseline posterior standard deviations and the other two by less than 0.01, leaving the top-three risk ranking unchanged. The count of ten floored readings quoted in Section 3.1.3 censuses the reference realisation; the displacement is a median over the thirty.

### 3.3.3 Bulk and wall decay compensate for one another

Fixing bulk decay at a wrong value transfers the error into the wall coefficients. Refitting with bulk decay 20% weaker or stronger than the truth, while the observations remain generated at the true value, displaced the average and new coefficients by 1.41 to 1.58 baseline posterior standard deviations and the old coefficient by only 0.56 to 0.66. The informal comparator understated these displacements by factors of 3.8 to 5.5, so that formulation would materially understate the apparent sensitivity to bulk-decay misspecification.

The Fisher analysis explains the pattern and extends it. Admitting bulk decay as a fourth unknown raises the Cramér–Rao bound from 25%, 29% and 29% of the prior standard deviation to 30%, 54% and 54%: the old bound widens by a factor of 1.2, whereas the average and new bounds widen by 1.8 and 1.9. Admitting six monitor-specific offsets as further nuisance parameters raises the ratios to 67%, 224% and 109%, so their local bounds equal or exceed the prior standard deviation. Under the identifiability criterion adopted here, the average and new coefficients are therefore not practically identifiable from this six-monitor design once both bulk decay and monitor offsets are treated as unknown. This is a statement about this observation design and nuisance model, not a mathematical impossibility. This is the formal counterpart of Section 3.3.2: the available concentration sensitivities do not separate the weakly decaying zones’ wall coefficients from bulk decay and monitor-specific offsets under a six-monitor design.

None of these perturbations is visible in the aggregate residual: the best fit reachable anywhere in the candidate library stays within a few percent of the realised observation-noise RMSE in every case, as the Best fit column of Table 4 records. These displacements are large in parameter terms, but Section 3.6 shows that they do not translate into proportionate changes in the network-wide risk pattern, and that whether an operational shortlist changes at all depends on which risk metric defines it. Before that, Section 3.4 turns to the one error source that is internal to the model rather than to the instruments.

Figure 4. Standardised effect of each error source. (A) Interval widening where an uncertainty source is represented in the model. (B) Displacement where a perturbation is imposed but not represented, in baseline posterior standard deviations. Columns aggregate differently, over 30 realisations, 25 fields, 24 bias arms and one paired draw, as the figure note defines.

| Error source | old | average | new | Best fit | Risk | Basis |
| --- | --- | --- | --- | --- | --- | --- |
| sigma 0.10 to 0.15 (W) | x1.41 | x1.52 | x1.48 | — | — | 30 real. |
| AR(1) rho = 0.4 (W) | x1.48 | x1.49 | x1.44 | — | — | Fisher |
| k_b = -0.4 (D) | -0.66 | -1.53 | -1.58 | 0.996 | rho_s 0.976; top-6 0.50 / 1.00 | 30 real. |
| k_b = -0.6 (D) | +0.56 | +1.41 | +1.49 | 0.997 | rho_s 0.933; top-6 0.50 / 0.71 | 30 real. |
| sensor bias, max over arms (D) | +3.87 | -5.94 | -4.44 | 0.995-1.062 | rho_s >= 0.9993; E[A] top-6 held in 23/24 | 24 arms x 30; max taken per coefficient |
| sensor drift (D) | 0.89-0.99 of the mean-equivalent bias |  |  | — | unchanged | 2 nodes x 4 |
| zero censoring (D) | -0.11 | -0.00 | +0.01 | — | top-3 unchanged | 30 real.; reference seed has 10/294 clipped |
| symmetric heterogeneity (D) | +0.11 | +0.02 | -0.06 | — | — | 25 fields |
| structured heterogeneity (D) | -1.55 | -1.89 | -1.65 | 0.995 | — | 1 design, single draw |

Notes

(W) widening, a factor on the interval; (D) displacement, in baseline posterior standard deviations.

Best fit: the smallest RMSE reachable anywhere in the candidate library under that perturbation, as a multiple of the realised observation-noise RMSE of the same draw. A value near one means the perturbation is not visible in the aggregate residual.

Risk column: whole-network Spearman, then top-6 Jaccard under P / E[A].

Structured-heterogeneity displacements are a single noise draw. Over 30 draws the median proxy-gap fraction is 0.86/1.12/0.92 (raw), with 5-95% intervals that overlap across zones, so the zones cannot be ordered against one another.

Length is one correlate; the length-weighted proxy is not the effective coefficient.

Table 4. Robustness summary across error sources. Standardisation follows Figure 4. The notes below the table define the entry types.

## 3.4 Structural heterogeneity and grouped effective parameters

### 3.4.1 Symmetric within-zone heterogeneity leaves no resolvable bias

Sections 3.2 and 3.3 treated each synthetic zone as internally homogeneous, whereas in the field wall reactivity is unlikely to be uniform within any practical grouping. Whether that variation biases the grouped estimate turns out to depend on whether it has directional structure.

With per-pipe coefficients jittered symmetrically about each zone mean, the grouped estimate stayed at the zone arithmetic mean to within the scatter between realisations. Across 25 independent fields at ±20%, the structural increment, defined as the shift relative to a homogeneous control run with the same noise, was +0.011 ± 0.033 m day-1 for old, +0.0002 ± 0.005 for average and −0.0005 ± 0.002 for new. Each mean increment is a fraction of the field-to-field standard deviation (0.32, 0.04 and 0.24), so no systematic bias is distinguishable from the scatter; standardised as in Figure 4 they are +0.11, +0.02 and −0.06.

Fit quality gives no warning: the grid-based residual rises from its homogeneous resolution floor of 0.0055 mg L-1 to 0.0068, leaving only 0.0013 attributable to the imposed heterogeneity, and the best achievable fit stays at the noise floor. Nor would one field have sufficed. The realisation examined first gave an old-zone increment of −0.032 m day-1, opposite in sign to the 25-field mean, as did the other two coefficients. What these 25 fields establish is therefore a negative result at the resolution of this design. No systematic mean displacement was resolvable against the field-to-field scatter under the fixed observation-noise realisation used throughout, which is weaker than a demonstration that symmetric jitter cancels exactly, and establishing even that required a paired control and replication over fields.

### 3.4.2 Structured heterogeneity displaces all three grouped coefficients

Heterogeneity correlated with a network property behaves differently. Making within-zone decay increase with pipe length while holding each zone’s arithmetic mean fixed separates two candidate targets for a homogeneous grouped fit, the arithmetic mean and a length-weighted directional comparator. In the paired reference realisation the control-adjusted displacements were −1.55, −1.89 and −1.65 baseline posterior standard deviations for old, average and new, while the best RMSE remained 0.0968 mg L-1 against a realised noise RMSE of 0.0973.

Across 30 noise realisations at λ=0.50 the median raw fractions of the arithmetic-to-length-weighted gap travelled were 0.86, 1.12 and 0.92. Their 5th-to-95th ranges overlap and all contain unity, so the zones cannot be ordered by displacement magnitude; the apparent average-zone overshoot in Figure 5C is not stable across draws. At λ=0.75 all three intervals exclude zero, resolving movement in the length-weighted direction but not its size.

The informal comparator did not attenuate the effect uniformly. For the old zone it returned only 46% to 59% of the formal displacement at every non-zero amplitude, whereas the average-zone informal fraction exceeds the formal one at λ=0.25 and 0.50 and the new-zone attenuation is mild throughout. The effect of the informal rule is therefore zone-specific: where it does attenuate, a study relying on it would understate how far structural misspecification moves that coefficient, but the halving seen for old cannot be assumed for the weakly decaying zones. The full amplitude sweep is reported in Table E4.

Figure 5. Symmetric and structured within-zone heterogeneity. Increments in (A) and (B) are in baseline posterior standard deviations. The displacement fraction fj in (C) is raw, summarised by median and 5–95% range over 30 noise realisations, with the single control-adjusted reference realisation marked faintly.

## 3.5 Predictive accuracy is not parameter identification

### 3.5.1 Leaving out one monitor

Withholding each of the six monitors in turn and refitting gives held-out RMSEs between 0.092 and 0.103 mg L-1 against an observation noise standard deviation of 0.1, with 90% predictive interval coverage between 0.90 and 0.94 (Table 5). Taken at face value, these diagnostics indicate good held-out predictive performance at all six monitors.

Two observations qualify that reading. Each zone retains its second monitor throughout, so the test establishes prediction at an unseen monitor while its zone remains locally observed. And the informal comparator achieved almost the same held-out RMSE, 0.092 to 0.102 mg L-1, despite the much broader parameter distributions of Section 3.2, so a weighting rule can extract very little parameter information and still predict concentrations about as well.

### 3.5.2 Leaving out a whole zone

Withholding both monitors of a zone removed the local update for the old and average coefficients. Both returned to their prior midpoints to three decimal places and retained 100% of the prior standard deviation. The new coefficient retained about 57%, consistent with its upstream position and with the cross-zone sensitivity visible in the Fisher analysis of Section 3.3.3.

Held-out prediction nevertheless stayed near the noise scale, with RMSEs of 0.0999, 0.0988 and 0.1006 mg L-1 and coverage between 0.90 and 0.96 (Figure 6). Repeating the design under ±20% per-pipe heterogeneity across eight independent fields produced the same qualitative separation, with errors at unmonitored junctions between 0.8% and 1.2%. In a separate spatial validation using all six monitors, predictions at twenty junctions that never entered any calibration had a median normalised mean absolute error of 0.83% under the primary likelihood, with an interquartile range of 0.41% to 1.45%.

The predictive bands at those junctions are less flattering and are reported for that reason. Against a nominal 90%, median pointwise coverage was 1.00 under both band constructions and both weighting rules, so the bands are conservative rather than calibrated in this model-matched design, and the same caution applies to the nominally well-calibrated coverage of the held-out monitor designs. Cross-coefficient compensation was small, the largest shift in a retained coefficient being 0.0086 m day-1. For old and average the prior midpoints lie close enough to the imposed truths that a prior-dominated coefficient still predicts within the 0.1 mg L-1 noise scale, whereas the new coefficient retains genuine information from monitors outside its own zone. Good held-out prediction therefore did not imply local parameter identification.

### 3.5.3 What predictive validation does and does not license

Held-out prediction supports spatial prediction at unseen locations within the same simulated operating regime. It does not support physical interpretation of the coefficients, attribution of decay to particular assets, or any intervention whose design depends on which zone is reactive. For those, Section 3.5.2 shows the evidence may be absent while every predictive diagnostic passes. Nor is any of this an external validation, for the reasons set out in Section 3.7.3.

Figure 6. Leave-one-zone-out parameter and prediction results. Left, median coefficient over 30 realisations against prior support, midpoint and truth; the bar is the median within-realisation posterior standard deviation at a Gaussian 90% width. Right, held-out RMSE against the 0.1 mg L-1 noise scale, bars showing the interquartile range.

| Design | Withheld | Own-coefficient error | Own SD retained | Held-out RMSE | Coverage |
| --- | --- | --- | --- | --- | --- |
| leave-one-monitor-out | node 107 (new) | - | - | 0.0978 | 0.92 |
| leave-one-monitor-out | node 113 (new) | - | - | 0.1026 | 0.90 |
| leave-one-monitor-out | node 15 (old) | - | - | 0.0938 | 0.94 |
| leave-one-monitor-out | node 145 (old) | - | - | 0.0922 | 0.94 |
| leave-one-monitor-out | node 209 (average) | - | - | 0.0987 | 0.91 |
| leave-one-monitor-out | node 231 (average) | - | - | 0.0990 | 0.92 |
| leave-one-zone-out | old zone (15, 145) | +0.1492 | 100% | 0.0999 | 0.96 |
| leave-one-zone-out | average zone (209, 231) | -0.0200 | 100% | 0.0988 | 0.92 |
| leave-one-zone-out | new zone (107, 113) | +0.0007 | 57% | 0.1006 | 0.90 |

Table 5. Held-out validation under the primary likelihood. Own-coefficient error is measured against the true zone value.

## 3.6 Propagation to operational low-chlorine risk

### 3.6.1 Duration, depth and hydraulic interpretation

The ensemble was propagated to all 92 junctions and summarised with several metrics rather than one. The values in this section carry the baseline weights and are conditional on its single reference observation realisation. Node 145 spends 12.0 h below 0.2 mg L-1, accumulates a deficit of 1.68 mg L-1 h and has a median window minimum of 0.031 mg L-1; node 129 spends twice as long below the threshold yet accumulates only 0.84 mg L-1 h, with a median minimum of 0.147. Duration measures persistence and deficit combines it with depth, so the two rank the network differently; a window-breach probability distinguishes neither, collapsing both to whether the threshold is crossed at all.

The population matters as much as the metric. Averaged over all 92 junctions the expected duration is 3.43 h; over the 59 that serve demand, 4.46 h; weighted by average expected demand, 1.23 h. The demand-weighted figure is lowest because low-chlorine conditions concentrate at small-demand junctions at network extremities, so reporting it alone would downweight exactly those locations.

Mean water age is associated with both metrics, with Spearman correlations of 0.73 against duration and 0.72 against deficit; for the duration association a ten-block spatial bootstrap gives a descriptive 95% width of [0.455, 0.897]. No p-value is quoted, because the junctions share pipes, tanks and demand patterns and are not independent samples. Water age is a hydraulic diagnostic from the same model rather than an independent measurement, and its absolute values remain horizon-dependent (Section 3.1.2), so the association is descriptive only.

### 3.6.2 Network-scale stability does not guarantee shortlist stability

The parameter displacements of Section 3.3 are large, but they do not propagate proportionately (Table 4). Under a 20% error in bulk decay the whole-network rank correlation stays between 0.93 and 0.98 on both risk metrics, and under any of the 24 sensor-bias arms it never falls below 0.9993. On that evidence the risk map looks robust.

The six-node shortlist an operator would act on behaves differently, and differently again by metric. Ranked by time-averaged below-threshold probability, a 20% bulk-decay error retains only four of the six leading nodes in either direction. Ranked by cumulative deficit, the same perturbation leaves the shortlist unchanged when bulk decay is underestimated and exchanges one boundary node when it is overestimated. Sensor bias is similar: nine of the 24 arms alter the duration-based shortlist, all positive offsets, whereas the deficit-based one is unchanged in 23 of 24. Changing the weighting rule rather than the physics has comparable effect, the two ensembles sharing nine of ten leading nodes.

Two claims must therefore be kept apart: a high whole-network rank correlation does not license the statement that the hot-spot list is stable, and any claim that hot spots did or did not change is meaningless without naming the metric behind it. Part of the duration ranking’s volatility comes from near-ties at the shortlist boundary, where three nodes lie within 0.001 of one another in expected breach fraction, but bulk-decay misspecification also produces deeper reordering. One node moves from third to eighth and another from fourth to twentieth when bulk decay is underestimated, and a node ranked twelfth rises to second when it is overestimated. The deficit ranking retains a more clearly separated leading core.

### 3.6.3 Temperature, ageing and dosing stress tests

Propagating the same ensemble through warmer conditions illustrates the machinery under illustrative stress-test assumptions. Adding the prescribed temperature uncertainty at the 12 degree Celsius baseline moves the network-mean cumulative deficit only from 0.218 to 0.222 mg L-1 h, leaving the breach count and demand at risk unchanged.

Raising the water temperature to 16 and then 20 degrees Celsius with Arrhenius scaling increases the number of junctions more likely than not to breach from 21 to 28 and 29, the demand they serve from 55.4 to 64.7 and 67.8 L s-1, and the network-mean cumulative deficit from 0.222 to 0.365 and 0.522 mg L-1 h. Adding illustrative zone-specific ageing multipliers at 20 degrees, 1.35 for the average zone and 1.85 for the old zone with the new zone unchanged, raises these to 31 junctions, 69.4 L s-1 and 0.579 mg L-1 h. The continuous severity measures respond more smoothly than the binary count, which is threshold-sensitive by construction.

Raising the source dose by 15% and 30% under the heatwave, applied to the reservoir boundary concentration and to the tank initial concentration together so that the whole source regime moves consistently, reduces the network-mean expected duration from 5.22 to 4.63 and 4.29 h and the deficit from 0.522 to 0.453 and 0.396 mg L-1 h, but demand at risk falls only to 64.7 L s-1 at both doses and never returns to the baseline 55.4. The identical figure at both doses is a plateau of the binary classification, not evidence that the extra 15% achieved nothing. The ageing multipliers are illustrative, no by-product, taste or booster constraint is represented, and absolute severities inherit the horizon dependence of Section 3.1.2. Maps and the full register are in Appendix H.

Figure 7. Risk robustness is metric-specific. (A) Rank of the leading nodes under P=E[D]/48 against cumulative deficit E[A]. (B) Top-six overlap with the reference ranking under three selected perturbations, each over 30 noise realisations, both metrics. (C) Expected duration against deficit for all 92 junctions.

## 3.7 Integrated implications, limitations and future work

Four qualifications recur across the results and are stated once here rather than repeated at each occurrence. Intervals from different diagnostics carry different nominal levels and are not a nested comparison. Interval widening and displacement answer different questions and are not on a common scale. The length-weighted value is a directional comparator, not an estimand, a common endpoint or a bound. The temperature, ageing and dosing results are calibration-conditioned stress tests under the stated assumptions, not forecasts, and the water-age association is descriptive rather than a significance test.

### 3.7.1 Parameter, prediction and decision robustness are distinct

Three findings sit at different levels and should not substitute for one another. At the level of the parameters, six monitors do carry identifiable information about all three coefficients under the controlled baseline; the contrary appearance in the original analysis arose from its specific informal weighting rather than from an absence of information in the monitored series.

At the level of robustness the error sources act in three ways, and a single verdict would mislead. Larger random error and an assumed AR(1) correlation mainly reduce precision. Systematic sensor error and structured heterogeneity instead introduce potentially large bias while leaving two separate things intact: the posterior stays narrow, and the aggregate residual stays near the noise level. Neither is evidence about the other, and neither reveals the bias. Bulk-decay uncertainty does both, disproportionately for the average and new coefficients; once it and six monitor offsets are all unknown, the Fisher analysis no longer supports practical identification of those two from this design.

At the level of decisions, neither predictive accuracy nor the whole-network risk pattern tracks parameter error reliably. Coefficients can become effectively prior-dominated while held-out prediction errors stay close to the observation-noise scale, and under bulk-decay misspecification and sensor bias, displacements of several posterior standard deviations often left the leading set ranked by cumulative deficit unchanged while the ranking by time-averaged breach probability was considerably more sensitive.

A study reporting only a fit statistic, a held-out prediction error or a rank correlation cannot distinguish a calibration that has learned its parameters from one that has learned to predict without them, or one whose broad ranking is stable while its shortlist is not.

### 3.7.2 Methodological implications

Four safeguards were necessary in these experiments, each following from a result above rather than from general good practice. Paired controls: a structural increment is interpretable only against a homogeneous run sharing the same noise, since part of any apparent shift is the inference rule’s own offset. Replication: the structural increment in one heterogeneity field reversed sign relative to the 25-field mean, and an apparent overshoot past the length-weighted comparator in one noise draw did not survive 30 realisations. Triangulation: prior contraction, a displaced prior, a curvature bound, a profile interval and a repeated-sampling experiment fail differently, so their agreement is far stronger than any one alone. Matching the metric to the claim: predictive RMSE does not test identification, a rank correlation does not test shortlist stability, and the low-chlorine metrics are not interchangeable.

### 3.7.3 Limitations

Synthetic and internally validated. Truth and calibration share the same hydraulics, reaction family and solver, and no field data are used. The priors were chosen to contain the synthetic truths and lie reasonably close to them; this suits a controlled experiment but makes prior-dominated predictions less damaging than under a poorly centred field prior, which bounds the generality of the leave-one-zone-out result in particular.

Idealised uncertainty representation. The observation standard deviation is known, baseline errors are independent, the autocorrelation coefficient is assumed rather than estimated, drift is a linear ramp, sensor offsets are imposed one at a time, and bulk decay is varied as a fixed sensitivity rather than inferred.

Fixed structure and hydraulics. The zones are synthetic, only one structured design was tested, and the effective weighting the fit estimates was not identified. Hydraulic uncertainty was not propagated at all, because demands, roughness, controls and the flow field were treated as known. The identifiability reported here is therefore likely optimistic relative to a field application where hydraulic and reaction parameters are uncertain together.

Bounded numerical and operational scope. The 120 h warm-up satisfies the chlorine-concentration criteria but not the water-age or cumulative-deficit criteria within the 168 h horizon, so absolute water-age and severity magnitudes remain horizon-dependent even though the concentration field underlying the inference results is stable. The baseline weighted ensemble has an effective sample size of about 157, and the sigma <= 0.05 mg L-1 rows are sampling-limited. Scenario inputs are illustrative, and 0.2 mg L-1 is a representative operational threshold, not a compliance limit.

### 3.7.4 Future work

Each extension addresses a failure mode identified above. The inference model should absorb what is currently fixed: bulk decay inferred jointly with the wall coefficients, monitor bias and drift as hierarchical nuisance parameters, and an estimated rather than assumed error covariance, which is costly in precision but honest about it. A likelihood-adapted sampler would remove the effective-sample-size collapse that made the low-noise cases uninformative. A sensitivity-weighted effective coefficient would establish what a grouped fit estimates, and siting monitors on the marginal Fisher information after nuisance adjustment, rather than on spatial coverage, addresses the Case C result directly. External validity requires both propagating hydraulic uncertainty and a real network with independent observations.

# 4. Conclusions

Under the controlled baseline assumptions, six monitored chlorine series carry identifiable information about all three grouped wall-decay coefficients. The formal censored likelihood contracted each coefficient to roughly a quarter to a third of its prior standard deviation, recovered a displaced prior, and agreed with a separately computed local Fisher bound, a continuous profile likelihood and a repeated-noise experiment. The much wider distributions obtained previously on the same system reflect the specific informal weighting used rather than an absence of information in the observations, and tightening its behavioural threshold does not close the gap, because a threshold cannot restore an omitted information factor.

That baseline result is conditional, and the conditions matter unequally. Larger random measurement error and an assumed temporal correlation mainly cost precision. Systematic sensor error, bulk-decay misspecification and structured within-zone heterogeneity instead displace the estimate by several posterior standard deviations while leaving the aggregate residual near the noise level, so in the cases tested here none of the three was revealed by that statistic. Bulk-decay uncertainty costs precision as well, disproportionately for the two weakly decaying zones; under the local Fisher analysis and the study-specific criterion that the Cramér–Rao bound stay below the prior standard deviation, those two coefficients cease to be practically identifiable from this six-monitor design once bulk decay and monitor-specific offsets are treated as unknown together.

Neither predictive accuracy nor the whole-network risk pattern is a reliable proxy for parameter recovery. When a zone’s monitors were withheld, the old- and average-zone coefficients returned to their prior midpoints and retained essentially the whole prior standard deviation, yet held-out prediction at those same monitors stayed at the observation-noise scale. Parameter displacements of several standard deviations left whole-network rank correlations high, but the six-node shortlist an operator would act on changed under some perturbations and not others, and which it was depended on whether the ranking used expected duration or cumulative deficit.

Three practical conclusions follow for calibration practice. The inference rule should be audited before a wide parameter distribution is read as evidence about the monitoring array. Systematic instrument error and model aggregation deserve at least the attention usually given to sensor precision, since they bias rather than merely blur. And parameter identification, predictive adequacy and decision stability should be reported separately, because a study that reports only one of them cannot show that the other two hold. These conclusions are established within a controlled synthetic experiment with known truth, fixed hydraulics and no field data, and their transfer to a real network remains to be tested.

# References

Beven, K. & Binley, A. (1992) The future of distributed models: Model calibration and uncertainty prediction. Hydrological Processes. 6(3), 279–298. 10.1002/hyp.3360060305.

Beven, K. & Binley, A. (2014) GLUE: 20 years on. Hydrological Processes. 28(24), 5897–5918. 10.1002/hyp.10082.

Brun, R., Reichert, P. & Künsch, H.R. (2001) Practical identifiability analysis of large environmental simulation models. Water Resources Research. 37(4), 1015–1030. 10.1029/2000WR900350.

Hallam, N.B., West, J.R., Forster, C.F., Powell, J.C. & Spencer, I. (2002) The decay of chlorine associated with the pipe wall in water distribution systems. Water Research. 36(14), 3479–3488. 10.1016/S0043-1354(02)00056-8.

Klise, K.A., Bynum, M., Moriarty, D. & Murray, R. (2017) A software framework for assessing the resilience of drinking water systems to disasters with an example earthquake case study. Environmental Modelling & Software. 95, 420–431. 10.1016/j.envsoft.2017.06.022.

Mantovan, P. & Todini, E. (2006) Hydrological forecasting uncertainty assessment: Incoherence of the GLUE methodology. Journal of Hydrology. 330(1–2), 368–381. 10.1016/j.jhydrol.2006.04.046.

Munavalli, G.R. & Mohan Kumar, M.S. (2003) Water quality parameter estimation in steady-state distribution system. Journal of Water Resources Planning and Management. 129(2), 124–134. 10.1061/(ASCE)0733-9496(2003)129:2(124).

Nejjari, F., Puig, V., Pérez, R., Quevedo, J., Cugueró, M.A., Sanz, G. & Mirats, J.M. (2014) Chlorine decay model calibration and comparison: Application to a real water network. Procedia Engineering. 70, 1221–1230. 10.1016/j.proeng.2014.02.135.

Powell, J.C., Hallam, N.B., West, J.R., Forster, C.F. & Simms, J. (2000) Factors which control bulk chlorine decay rates. Water Research. 34(1), 117–126. 10.1016/S0043-1354(99)00097-4.

Raue, A., Kreutz, C., Maiwald, T., Bachmann, J., Schilling, M., Klingmüller, U. & Timmer, J. (2009) Structural and practical identifiability analysis of partially observed dynamical models by exploiting the profile likelihood. Bioinformatics. 25(15), 1923–1929. 10.1093/bioinformatics/btp358.

Rossman, L.A. (2000) EPANET 2 users manual. Cincinnati, OH: U.S. Environmental Protection Agency.

Rossman, L.A., Clark, R.M. & Grayman, W.M. (1994) Modeling chlorine residuals in drinking-water distribution systems. Journal of Environmental Engineering. 120(4), 803–820. 10.1061/(ASCE)0733-9372(1994)120:4(803).

Rossman, L.A., Woo, H., Tryby, M., Shang, F., Janke, R. & Haxton, T. (2020) EPANET 2.2 user manual. Cincinnati, OH: U.S. Environmental Protection Agency.

Stedinger, J.R., Vogel, R.M., Lee, S.U. & Batchelder, R. (2008) Appraisal of the generalized likelihood uncertainty estimation (GLUE) method. Water Resources Research. 44(12), W00B06. 10.1029/2008WR006822.

Vasconcelos, J.J., Rossman, L.A., Grayman, W.M., Boulos, P.F. & Clark, R.M. (1997) Kinetics of chlorine decay. Journal AWWA. 89(7), 54–65. 10.1002/j.1551-8833.1997.tb08259.x.

# Appendices

Every table below is generated directly from the cached result artifacts by Net3/appendix_tables.py, so no appendix value can drift from the one the main text quotes. Appendix I maps each section of the paper to the script that produced its numbers.

## Appendix A. Warm-up length and the model horizon

Six cyclostationarity criteria were declared before the values were seen, each comparing a 24 h cycle with its successor across the truth and both corners of the prior box. Table A1 gives the worst value for each criterion at each cycle pair.

Three of the six are met at a 120 h warm-up and two are not. The horizon cannot be extended to settle them: pump 10 is driven by absolute-time controls enumerated only to 159 h against a model duration of 168 h, so a longer run is a different system rather than a longer warm-up. The integrated severity is still drifting at the horizon, and water age is horizon-dependent by construction in this network. Table A2 shows why the severity criterion fails, with the network-mean deficit falling after the start-up transient and then rising monotonically.

Table A1. Cyclostationarity diagnostics. Worst value across the truth and both corners of the prior box, for each pair of successive 24 h cycles. Tolerances were declared before the values were seen.

| Criterion | Tolerance | 0-24 | 24-48 | 48-72 | 72-96 | 96-120 | 120-144 | Earliest warm-up satisfying it |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Tank level (m) | 0.05 | 0.8185 | 0.0496 | 0.0070 | 0.0009 | 8.8e-05 | 8.4e-05 | 24 h (verified) |
| Monitor chlorine (mg L-1) | 0.005 | 0.9209 | 0.0437 | 0.0234 | 0.0122 | 0.0064 | 0.0034 | 120 h (verified) |
| Network 95th-percentile chlorine (mg L-1) | 0.01 | 0.9511 | 0.1061 | 0.0396 | 0.0201 | 0.0103 | 0.0054 | 120 h (verified) |
| Tank chlorine (mg L-1) | 0.01 | 0.2457 | 0.0787 | 0.0416 | 0.0219 | 0.0115 | 0.0061 | 120 h (verified) |
| Risk severity, relative change in E[A] | 0.02 | 0.8983 | 0.6104 | 0.1206 | 0.1897 | 0.0978 | 0.0509 | not met within 168 h; extrapolates to ~168 h (unverified) |
| Water age, 95th percentile (h) | 1.0 | 23.9990 | 21.6756 | 19.0425 | 16.6924 | 14.6298 | 12.8149 | not met within 168 h; extrapolates to ~600 h (unverified) |

Table A2. Network-mean cumulative deficit for the truth, by cycle. The integrated severity falls after the start-up transient and then rises monotonically, which is why the 2% criterion is not met inside the model horizon.

| Cycle | Net-mean deficit (mg L-1 h) | Relative change |
| --- | --- | --- |
| 0-24 h | 1.0050 | 0.8659 |
| 24-48 h | 0.1348 | 0.3911 |
| 48-72 h | 0.0821 | 0.1206 |
| 72-96 h | 0.0920 | 0.1194 |
| 96-120 h | 0.1029 | 0.0607 |
| 120-144 h | 0.1092 | 0.0308 |

## Appendix B. Numerical and unit verification

Table B1. Bulk-decay arm of the known-answer test against the analytic first-order solution at the far end of a single pipe. The relative error grows with the amount of decay, which is the signature of the quality solver’s time discretisation; a wrong conversion factor would instead give a constant relative offset.

| k_b (1/day) | Residence time (h) | EPANET C | Analytic C | Relative error |
| --- | --- | --- | --- | --- |
| -0.50 | 0.3927 | 0.991846 | 0.991852 | 6.7e-06 |
| -1.00 | 0.3927 | 0.983744 | 0.983771 | 2.7e-05 |
| -2.00 | 0.3927 | 0.967699 | 0.967805 | 1.1e-04 |

Table B2. Wall-decay arm. The exact concentration cannot be predicted from the wall coefficient alone because EPANET’s first-order wall reaction is also limited by mass transfer, so what is asserted is the sign, monotonicity, and that the result stays above the mass-transfer-free limit.

| k_w (m/day) | EPANET C | Extra decay vs k_w=0 | Mass-transfer-free bound | Above bound |
| --- | --- | --- | --- | --- |
| 0.00 | 0.991846 | 0.000000 | 0.991852 | n/a |
| -0.10 | 0.971232 | 0.020613 | 0.970448 | yes |
| -0.50 | 0.905719 | 0.086127 | 0.889350 | yes |
| -1.00 | 0.849034 | 0.142812 | 0.797441 | yes |
| -2.00 | 0.779180 | 0.212665 | 0.641136 | yes |

Table B3. Unit-equivalence test over 256 leading Sobol candidates. The corrected implementation reproduces the superseded one to floating-point precision. The units-only arm shows what correcting the concentrations while leaving the solver tolerance at the EPANET default would have cost.

| Comparison | Max absolute difference (mg L-1) | Max relative difference | Points below threshold | Duration cells that differ |
| --- | --- | --- | --- | --- |
| corrected vs legacy | 1.19e-07 | 2.33e-07 | 79391 -> 79391 | 0 of 23552 |
| units only vs legacy | 2.09e-02 | 1.78e-01 | 79391 -> 79301 | 440 of 23552 |

The tolerance was set to 1×10−5 mg L-1 rather than left at the EPANET default of 0.01 mg L-1. This is a chosen numerical setting, not a unit conversion: WNTR writes the tolerance into the input file verbatim while converting concentrations, so the file receives TOLERANCE 1e-05 and EPANET reads it in mg L-1. Holding the tolerance-to-source ratio fixed is what allows the corrected and superseded implementations to be compared as the same numerical experiment in Table B3.

A related defect is worth recording for anyone reusing this toolchain. The same root cause, that concentrations are converted on file write while some reaction coefficients are not, means a zero-order bulk coefficient passed through the WNTR 1.4 API arrives at EPANET unscaled while the concentrations around it have been scaled, giving reaction rates a thousand times smaller than nominal. First-order coefficients carry no mass unit and are unaffected, which is why the checks in Tables B1 and B2 pass either way.

## Appendix C. Threshold sweep and displaced-prior matrices

Table C1. Behavioural-threshold sweep for the informal comparator. Tightening the cut-off removes candidates but cannot restore the information factor the score omits, so the retained widths stay far above the formal values.

| Threshold (mg L-1) | Retained | Retention | SD above sigma | old SD (retained) | average SD (retained) | new SD (retained) |
| --- | --- | --- | --- | --- | --- | --- |
| 0.107 | 4786 | 58.4% | 1.70 | 0.2668 (71.1%) | 0.0424 (91.8%) | 0.0242 (88.2%) |
| 0.110 | 5668 | 69.2% | 2.42 | 0.2844 (75.8%) | 0.0437 (94.5%) | 0.0254 (92.7%) |
| 0.120 | 7084 | 86.5% | 4.85 | 0.3220 (85.8%) | 0.0455 (98.4%) | 0.0269 (98.0%) |

Table C2. Displaced-prior recovery over 30 noise realisations, as the median fraction of the imposed displacement recovered with its interquartile range, and the retained prior width. DOWN displaces every coefficient towards stronger decay; OLDUP displaces the old coefficient the other way.

| Design | Rule | Coefficient | Displacement recovered [IQR] | Prior SD retained |
| --- | --- | --- | --- | --- |
| DOWN | formal censored | old | 88% [67-104] | 27% |
| DOWN | formal censored | avg | 95% [75-110] | 29% |
| DOWN | formal censored | new | 96% [80-122] | 28% |
| DOWN | informal glue@0.107 | old | 28% [14-55] | 92% |
| DOWN | informal glue@0.107 | avg | 43% [27-58] | 87% |
| DOWN | informal glue@0.107 | new | 78% [56-82] | 65% |
| DOWN | informal glue@0.12 | old | 9% [5-13] | 99% |
| DOWN | informal glue@0.12 | avg | 14% [10-19] | 97% |
| DOWN | informal glue@0.12 | new | 23% [14-32] | 92% |
| OLDUP | formal censored | old | 112% [95-132] | 25% |
| OLDUP | formal censored | avg | 95% [75-111] | 29% |
| OLDUP | formal censored | new | 96% [80-122] | 29% |
| OLDUP | informal glue@0.107 | old | 85% [75-94] | 52% |
| OLDUP | informal glue@0.107 | avg | 43% [29-60] | 88% |
| OLDUP | informal glue@0.107 | new | 66% [42-71] | 69% |
| OLDUP | informal glue@0.12 | old | 61% [54-64] | 68% |
| OLDUP | informal glue@0.12 | avg | 15% [10-20] | 97% |
| OLDUP | informal glue@0.12 | new | 14% [9-21] | 95% |

## Appendix D. Fisher information mechanics

Bounds for the three wall-decay coefficients under nested nuisance models are computed from the marginal information, that is the Schur complement Fpp−FpnFnn−1Fnp, where p indexes the wall coefficients and n the nuisance parameters admitted in that case. This is the bound on the wall coefficients after the nuisance parameters have been accounted for, not the bound that would apply if they were known.

Table D1. Cramer-Rao bounds under nested nuisance models, obtained from the marginal (Schur) information. Percentages are the bound as a fraction of the prior standard deviation.

| Case | Condition number | old | average | new |
| --- | --- | --- | --- | --- |
| A: kw only | 214.7 | 0.0947 (25%) | 0.0135 (29%) | 0.0080 (29%) |
| B: kw+kb | 100.5 | 0.1131 (30%) | 0.0248 (54%) | 0.0148 (54%) |
| C: kw+kb+6 offsets | 88.0 | 0.2509 (67%) | 0.1036 (224%) | 0.0299 (109%) |

Table D2. Finite-difference step convergence for the Jacobian. Steps are scale-dependent rather than shared, because one absolute step would be a 2% perturbation of the old coefficient and a 40% perturbation of the new one.

| Coefficient | Step | As % of truth | Default | Case-A bound |
| --- | --- | --- | --- | --- |
| old | 0.005 | 0.5% |  | 0.094819 |
| old | 0.01 | 1.0% |  | 0.094816 |
| old | 0.02 | 2.0% | yes | 0.094734 |
| old | 0.04 | 4.0% |  | 0.094724 |
| average | 0.002 | 2.0% |  | 0.013534 |
| average | 0.005 | 5.0% | yes | 0.013509 |
| average | 0.01 | 10.0% |  | 0.013487 |
| average | 0.02 | 20.0% |  | 0.013400 |
| new | 0.001 | 2.0% |  | 0.008030 |
| new | 0.0025 | 5.0% | yes | 0.007956 |
| new | 0.005 | 10.0% |  | 0.007955 |
| new | 0.01 | 20.0% |  | 0.007940 |

Table D3. Eigenvalues of the Case-A information matrix in raw and prior-scaled form. The raw condition number is dominated by the factor of twenty between the coefficient scales; on the dimensionless matrix the spread is far smaller.

| Form | Eigenvalue 1 | Eigenvalue 2 | Eigenvalue 3 | Condition number |
| --- | --- | --- | --- | --- |
| Raw | 23906 | 5106 | 111 | 215 |
| Prior-scaled | 24.5 | 16.6 | 7.6 | 3.2 |

Table D4. Case-A bounds under an assumed AR(1) residual covariance, swept over the correlation parameter. The correlation is assumed rather than estimated, since the baseline observations are generated independently; the sweep therefore bounds how much the reported precision would degrade if the residuals were in fact correlated. Widening is the bound relative to the independent case, given for old, average and new. The three coefficients widen almost together up to a correlation of 0.4 and separate beyond it, the new coefficient least and the average coefficient most.

| Correlation | Effective n | old | average | new | Widening (old / avg / new) |
| --- | --- | --- | --- | --- | --- |
| 0.0 | 294 | 0.0947 (25%) | 0.0135 (29%) | 0.0080 (29%) | 1.00 / 1.00 / 1.00 |
| 0.2 | 196 | 0.1150 (31%) | 0.0164 (35%) | 0.0096 (35%) | 1.21 / 1.21 / 1.20 |
| 0.4 | 126 | 0.1406 (37%) | 0.0201 (43%) | 0.0114 (42%) | 1.48 / 1.49 / 1.44 |
| 0.6 | 74 | 0.1736 (46%) | 0.0252 (55%) | 0.0135 (49%) | 1.83 / 1.87 / 1.70 |
| 0.8 | 33 | 0.2022 (54%) | 0.0333 (72%) | 0.0145 (53%) | 2.13 / 2.47 / 1.82 |

## Appendix E. Structural heterogeneity: definitions and per-design results

Four quantities are reported for the heterogeneity experiments and are easy to confuse. The raw bias is the weighted posterior mean minus the true per-zone arithmetic mean. The structural increment subtracts the corresponding homogeneous control run on the same noise, and is the part attributable to the imposed structure rather than to the realisation. The standardised displacement divides by the median within-realisation posterior standard deviation of the unperturbed reference. The displacement fraction is the position of the fit between the two candidate targets, the arithmetic mean and the length-weighted value, and is undefined where they coincide.

Table E1. Symmetric within-zone heterogeneity under the primary rule. The increment is the bias net of a paired homogeneous control run on the same noise, which is the part that can be attributed to the imposed structure.

| Jitter | Zone | True arithmetic mean | Raw bias | In posterior SD | Increment over control |
| --- | --- | --- | --- | --- | --- |
| 0% | old | -1.0000 | +0.0124 | +0.13 | +0.0000 |
| 0% | average | -0.1000 | -0.0091 | -0.64 | +0.0000 |
| 0% | new | -0.0500 | +0.0060 | +0.77 | +0.0000 |
| 20% | old | -1.0066 | -0.0200 | -0.20 | -0.0325 |
| 20% | average | -0.0978 | -0.0104 | -0.74 | -0.0012 |
| 20% | new | -0.0487 | +0.0071 | +0.93 | +0.0011 |
| 35% | old | -1.0115 | -0.0334 | -0.33 | -0.0458 |
| 35% | average | -0.0962 | -0.0108 | -0.78 | -0.0016 |
| 35% | new | -0.0478 | +0.0080 | +1.05 | +0.0020 |
| 50% | old | -1.0165 | -0.0366 | -0.36 | -0.0490 |
| 50% | average | -0.0946 | -0.0107 | -0.79 | -0.0016 |
| 50% | new | -0.0468 | +0.0089 | +1.18 | +0.0029 |

Table E2. The same design repeated over 25 independent heterogeneity fields at plus or minus 20%. The mean increment is a fraction of the field-to-field scatter in every zone, so no systematic bias is distinguishable from the choice of field.

| Zone | Bias mean | Bias SD | Increment mean | Increment SD |  |
| --- | --- | --- | --- | --- | --- |
| old | +0.0231 | 0.0335 | +0.0107 | 0.0335 | 0.32 |
| average | -0.0089 | 0.0046 | +0.0002 | 0.0046 | 0.04 |
| new | +0.0055 | 0.0021 | -0.0005 | 0.0021 | 0.24 |

Table E3. Length-structured heterogeneity in the reference realisation. The homogeneous baseline offset is what the same rule returns with no structural error at all and must be subtracted before a shift is read as structural.

| Zone | Rule | Arithmetic mean | Length-weighted proxy | Posterior mean | Shift | Homogeneous offset | Fraction of gap |
| --- | --- | --- | --- | --- | --- | --- | --- |
| old | formal censored | -1.0000 | -1.2404 | -1.1444 | -0.1444 | +0.0124 | 60% |
| old | informal glue | -1.0000 | -1.2404 | -1.0666 | -0.0666 | -0.0115 | 28% |
| average | formal censored | -0.1000 | -0.1238 | -0.1349 | -0.0349 | -0.0091 | 147% |
| average | informal glue | -0.1000 | -0.1238 | -0.1300 | -0.0300 | -0.0170 | 126% |
| new | formal censored | -0.0500 | -0.0659 | -0.0571 | -0.0071 | +0.0060 | 45% |
| new | informal glue | -0.0500 | -0.0659 | -0.0593 | -0.0093 | +0.0008 | 58% |

Table E4. Length-structured amplitude sweep over 30 noise realisations. Entries are the median raw displacement fraction with its 5 to 95% range, where 0 is the arithmetic zone mean and 1 the length-weighted reference. The fraction is undefined at an amplitude of zero because the two references coincide.

| Amplitude | old formal | old informal | average formal | average informal | new formal | new informal |
| --- | --- | --- | --- | --- | --- | --- |
| 0.00 | — | — | — | — | — | — |
| 0.25 | 1.10 [-0.29, 2.47] | 0.65 [-0.05, 1.11] | 1.26 [-0.95, 3.72] | 2.00 [1.12, 2.77] | 0.98 [-0.89, 2.66] | 0.89 [0.29, 1.52] |
| 0.50 | 0.86 [0.12, 1.46] | 0.43 [0.16, 0.69] | 1.12 [-0.07, 2.43] | 1.22 [0.98, 1.66] | 0.92 [-0.03, 1.78] | 0.78 [0.40, 1.08] |
| 0.75 | 0.74 [0.23, 1.06] | 0.34 [0.16, 0.52] | 1.07 [0.22, 1.93] | 0.97 [0.74, 1.26] | 0.89 [0.26, 1.46] | 0.72 [0.43, 0.92] |

## Appendix F. Per-arm sensor error and drift results

Table F1. Every arm of the sensor-bias sweep under the primary rule, as the displacement of each coefficient in baseline posterior standard deviations. Rank statistics compare the 92-junction risk field with the unbiased case.

| Node | Zone | Offset (mg L-1) | old | average | new | Censored points | Spearman | Top-6 Jaccard (duration) | Top-6 Jaccard (deficit) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 107 | new | -0.100 | +0.91 | +1.59 | -3.84 | 7 | 0.9997 | 1.00 | 1.00 |
| 113 | new | -0.100 | +1.01 | +1.82 | -4.44 | 7 | 0.9997 | 1.00 | 1.00 |
| 15 | old | -0.100 | -3.82 | +0.08 | +0.14 | 13 | 0.9995 | 1.00 | 1.00 |
| 145 | old | -0.100 | -3.31 | +0.48 | -0.80 | 12 | 0.9996 | 1.00 | 1.00 |
| 209 | average | -0.100 | +0.74 | -1.89 | -2.66 | 7 | 0.9997 | 1.00 | 1.00 |
| 231 | average | -0.100 | -0.29 | -5.94 | +0.74 | 7 | 0.9999 | 1.00 | 1.00 |
| 107 | new | -0.050 | +0.50 | +0.83 | -1.92 | 7 | 0.9997 | 1.00 | 1.00 |
| 113 | new | -0.050 | +0.57 | +0.97 | -2.24 | 7 | 0.9997 | 1.00 | 1.00 |
| 15 | old | -0.050 | -2.59 | -0.04 | +0.20 | 9 | 0.9997 | 1.00 | 1.00 |
| 145 | old | -0.050 | -1.89 | +0.19 | -0.34 | 9 | 0.9997 | 1.00 | 1.00 |
| 209 | average | -0.050 | +0.40 | -0.79 | -1.38 | 7 | 0.9999 | 1.00 | 1.00 |
| 231 | average | -0.050 | -0.17 | -3.25 | +0.59 | 7 | 0.9999 | 1.00 | 1.00 |
| 107 | new | +0.050 | -0.52 | -0.91 | +1.85 | 7 | 0.9997 | 0.71 | 1.00 |
| 113 | new | +0.050 | -0.59 | -1.02 | +2.08 | 7 | 0.9997 | 0.71 | 1.00 |
| 15 | old | +0.050 | +2.19 | +0.11 | -0.25 | 5 | 0.9995 | 0.71 | 1.00 |
| 145 | old | +0.050 | +1.59 | -0.16 | +0.34 | 4 | 0.9995 | 0.71 | 1.00 |
| 209 | average | +0.050 | -0.41 | +0.60 | +1.33 | 7 | 0.9999 | 1.00 | 1.00 |
| 231 | average | +0.050 | +0.11 | +2.72 | -0.59 | 7 | 1.0000 | 1.00 | 1.00 |
| 107 | new | +0.100 | -1.04 | -1.85 | +3.62 | 7 | 0.9997 | 0.71 | 1.00 |
| 113 | new | +0.100 | -1.13 | -2.02 | +3.97 | 7 | 0.9997 | 0.71 | 1.00 |
| 15 | old | +0.100 | +3.87 | +0.25 | -0.51 | 5 | 0.9993 | 0.71 | 0.71 |
| 145 | old | +0.100 | +2.95 | -0.31 | +0.66 | 4 | 0.9994 | 0.71 | 1.00 |
| 209 | average | +0.100 | -0.82 | +1.10 | +2.58 | 7 | 0.9997 | 0.71 | 1.00 |
| 231 | average | +0.100 | +0.05 | +4.22 | -0.58 | 7 | 1.0000 | 1.00 | 1.00 |

Table F2. Sensor drift against its mean-equivalent and end-equivalent constant-bias controls on identical noise. A monotone drift acts, to within about a tenth, as a constant bias at its mean over the window.

| Node | End offset D | Drift shift | const(D/2) | const(D) | Drift / const(D/2) | Drift / const(D) |
| --- | --- | --- | --- | --- | --- | --- |
| 15 | -0.100 | -0.2370 | -0.2623 | -0.3869 | 0.90 | 0.61 |
| 15 | -0.050 | -0.1187 | -0.1339 | -0.2623 | 0.89 | 0.45 |
| 15 | +0.050 | +0.1061 | +0.1174 | +0.2213 | 0.90 | 0.48 |
| 15 | +0.100 | +0.2017 | +0.2213 | +0.3919 | 0.91 | 0.51 |
| 231 | -0.100 | -0.0435 | -0.0443 | -0.0810 | 0.98 | 0.54 |
| 231 | -0.050 | -0.0207 | -0.0211 | -0.0443 | 0.98 | 0.47 |
| 231 | +0.050 | +0.0192 | +0.0196 | +0.0371 | 0.98 | 0.52 |
| 231 | +0.100 | +0.0366 | +0.0371 | +0.0575 | 0.99 | 0.64 |

## Appendix G. Risk-assessment mechanics

Table G1. Water-age association and the resampling design behind its interval. Whole spatial blocks are resampled rather than individual junctions, because junctions sharing pipes, flow paths and tank states are not independent samples. The interval is a descriptive width, not a significance test.

| Quantity | Value |
| --- | --- |
| Spearman, duration | 0.7285 |
| Spearman, deficit | 0.7219 |
| Pearson, duration | 0.8611 |
| Junctions | 92 |
| Blocks | 10 |
| Block rule | k-means on standardised node coordinates; whole blocks resampled with replacement |
| Resamples | 2000 |
| 95% interval, Spearman duration | [0.455, 0.897] |

Table G2. Three network averages for each risk metric. Consumer-only is worse than unweighted while demand-weighted is better, which can only happen if the risk concentrates at small consumers.

| Metric | Unweighted (all 92) | Consumer-only (59) | Demand-weighted |
| --- | --- | --- | --- |
| E duration h | 3.4309 | 4.4610 | 1.2311 |
| E deficit | 0.2181 | 0.3053 | 0.0798 |
| min C | 0.4922 | 0.4412 | 0.6348 |

Table G3. Scenario draw specification. One draw per retained ensemble member is reused across every scenario and dose as a common random number, so scenario differences are physical rather than Monte Carlo noise.

| Quantity | Specification |
| --- | --- |
| Retained draws | 2196 of 8192 (weight above 1e-06 of the maximum) |
| Discarded weight mass | 3.79e-06 |
| Bulk activation energy | N(45000, 8000^2) J/mol, truncated below at 5000 |
| Realised bulk range | 17593 to 72051 J/mol |
| Wall activation energy | N(35000, 10000^2) J/mol, truncated below at 5000 |
| Realised wall range | 5103 to 70241 J/mol |
| Water temperature | dT ~ N(0, 1.0^2) added to the scenario mean, truncated to [-4.0, +4.0] degC so every scenario stays inside the 8.0-24.0 degC validity range |
| Realised temperature range | 8.48 to 23.50 degC |
| Draws resampled at the bound | 0 |
| Common random numbers | True |

## Appendix H. Risk banding and the full register

Table H1. Risk banding. The likelihood and severity axes are scored 1 to 5 on the criteria below and consequence 0 to 3; a risk score is the axis score times the consequence score, and the band follows from that score. The severity edges are pre-declared hours rather than quantiles of this network’s own results, so the same scale applies across scenarios. The governing band is the higher of the breach-probability band and the severity band, since neither axis alone may reduce an action.

| Axis | Band | Criterion |
| --- | --- | --- |
| Likelihood, from Pmin | rare | P_min < 0.05 |
|  | unlikely | 0.05 <= P_min < 0.20 |
|  | possible | 0.20 <= P_min < 0.50 |
|  | likely | 0.50 <= P_min < 0.80 |
|  | almost certain | P_min >= 0.80 |
| Severity, from E[D] | negligible | E[D] < 1 h |
|  | brief | 1 <= E[D] < 6 h |
|  | sustained | 6 <= E[D] < 12 h |
|  | prolonged | 12 <= E[D] < 24 h |
|  | persistent | E[D] >= 24 h (half the assessment window or more) |
| Consequence, from demand | non-consumer | d = 0, a non-consumer junction |
|  | minor | 0 < d <= 1.67 L/s |
|  | moderate | 1.67 < d <= 4.38 L/s |
|  | major | d > 4.38 L/s |
| Risk band, from score | not applicable | score = 0 |
|  | low | 1 <= score <= 3 |
|  | medium | 4 <= score <= 6 |
|  | high | 7 <= score <= 9 |
|  | very high | score >= 10 |

Table H2. The complete risk register, all 92 junctions, ordered by expected cumulative deficit. Bands are defined in Table H1.

| node | P min current | P min heatwave | P min heat ageing | demand L s | risk band severity | risk band governing |
| --- | --- | --- | --- | --- | --- | --- |
| 15 | 1.0 | 1.0 | 1.0 | 16.67 | very high | very high |
| 151 | 1.0 | 1.0 | 1.0 | 9.75 | high | very high |
| 247 | 1.0 | 1.0 | 1.0 | 4.75 | medium | very high |
| 131 | 1.0 | 1.0 | 1.0 | 2.88 | very high | very high |
| 145 | 1.0 | 1.0 | 1.0 | 1.86 | high | very high |
| 149 | 1.0 | 1.0 | 1.0 | 1.83 | medium | very high |
| 153 | 1.0 | 1.0 | 1.0 | 2.98 | high | very high |
| 253 | 1.0 | 1.0 | 1.0 | 3.68 | medium | very high |
| 255 | 1.0 | 1.0 | 1.0 | 2.73 | medium | very high |
| 125 | 0.998 | 1.0 | 1.0 | 3.08 | high | very high |
| 127 | 1.0 | 1.0 | 1.0 | 1.19 | medium | medium |
| 139 | 1.0 | 1.0 | 1.0 | 0.4 | medium | medium |
| 141 | 1.0 | 1.0 | 1.0 | 0.66 | medium | medium |
| 143 | 1.0 | 1.0 | 1.0 | 0.42 | medium | medium |
| 147 | 1.0 | 1.0 | 1.0 | 0.58 | low | medium |
| 243 | 1.0 | 1.0 | 1.0 | 0.29 | medium | medium |
| 251 | 1.0 | 1.0 | 1.0 | 1.63 | low | medium |
| 35 | 0.0 | 0.0 | 0.0 | 108.39 | low | low |
| 101 | 0.0 | 0.0 | 0.0 | 12.82 | low | low |
| 103 | 0.0 | 0.0 | 0.0 | 8.99 | low | low |
| 105 | 0.0 | 0.0 | 0.0 | 9.13 | low | low |
| 109 | 0.0 | 0.0 | 0.0 | 15.61 | low | low |
| 111 | 0.0 | 0.0 | 0.0 | 9.58 | low | low |
| 117 | 0.0 | 0.0 | 0.0 | 7.94 | low | low |
| 119 | 0.0 | 0.0 | 0.0 | 11.89 | low | low |
| 123 | 0.0 | 0.0 | 0.0 | 75.32 | low | low |
| 189 | 0.0 | 0.0 | 0.0 | 7.28 | low | low |
| 191 | 0.0 | 0.0 | 0.0 | 5.53 | low | low |
| 193 | 0.0 | 0.0 | 0.0 | 4.81 | low | low |
| 199 | 0.0 | 0.0 | 0.0 | 8.05 | low | low |
| 203 | 0.0 | 0.0 | 0.0 | 284.63 | low | low |
| 205 | 0.0 | 0.0 | 0.0 | 4.41 | low | low |
| 207 | 0.0 | 0.0 | 0.0 | 4.68 | low | low |
| 215 | 0.0 | 0.023 | 0.114 | 6.22 | low | low |
| 219 | 0.011 | 1.0 | 1.0 | 2.79 | low | low |
| 107 | 0.0 | 0.0 | 0.0 | 3.69 | low | low |
| 115 | 0.0 | 0.0 | 0.0 | 3.52 | low | low |
| 121 | 0.0 | 0.0 | 0.0 | 2.81 | low | low |
| 157 | 0.0 | 0.0 | 0.0 | 3.49 | low | low |
| 159 | 0.0 | 0.0 | 0.0 | 2.79 | low | low |
| 171 | 0.0 | 0.0 | 0.0 | 2.65 | low | low |
| 177 | 0.0 | 1.0 | 1.0 | 3.93 | low | low |
| 185 | 0.0 | 0.0 | 0.0 | 1.73 | low | low |
| 201 | 0.0 | 0.0 | 0.0 | 3.01 | low | low |
| 229 | 0.0 | 0.0 | 0.0 | 4.33 | low | low |
| 239 | 0.0 | 0.832 | 0.986 | 3.01 | low | low |
| 225 | 0.03 | 1.0 | 1.0 | 1.54 | low | low |
| 231 | 0.001 | 1.0 | 1.0 | 1.11 | low | low |
| 113 | 0.0 | 0.0 | 0.0 | 1.35 | low | low |
| 161 | 0.0 | 0.0 | 0.0 | 1.07 | low | low |
| 163 | 0.0 | 0.0 | 0.0 | 0.64 | low | low |
| 166 | 0.0 | 0.483 | 0.492 | 0.18 | low | low |
| 167 | 0.0 | 0.0 | 0.0 | 0.98 | low | low |
| 197 | 0.0 | 0.0 | 0.0 | 1.15 | low | low |
| 209 | 0.0 | 0.0 | 0.0 | 0.06 | low | low |
| 211 | 0.0 | 0.0 | 0.0 | 0.59 | low | low |
| 213 | 0.0 | 0.0 | 0.0 | 0.94 | low | low |
| 217 | 0.0 | 0.403 | 0.748 | 1.63 | low | low |
| 237 | 0.0 | 0.0 | 0.001 | 1.05 | low | low |
| 20 | 1.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 50 | 1.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 129 | 1.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 241 | 1.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 10 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 40 | 0.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 60 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 601 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 61 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 120 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 164 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 169 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 173 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 179 | 0.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 181 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 183 | 0.0 | 1.0 | 1.0 | 0.0 | not applicable | not applicable |
| 184 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 187 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 195 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 204 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 206 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 208 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 249 | 0.0 | 0.122 | 0.533 | 0.0 | not applicable | not applicable |
| 257 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 259 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 261 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 263 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 265 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 267 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 269 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 271 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 273 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |
| 275 | 0.0 | 0.0 | 0.0 | 0.0 | not applicable | not applicable |

## Appendix I. Section-to-script map and reproduction

The analysis code, the cached result artifacts and this paper’s figure and table generators are archived at

[REPOSITORY URL AND RELEASE TAG TO BE INSERTED BEFORE SUBMISSION]

and every number in this paper was produced at that release. The frozen Net3 input file is hash-checked on import, and the environment is pinned to exact library versions, which matters here because the study documents version-specific WNTR behaviour. The verification checks of Section 2.2.4 are runnable: provenance.py --check confirms that the environment matches the one that produced the cached results, and validate_artifacts.py cross-checks the written numbers against the artifacts.

Each script writes Net3/baseline_cache/<script name>.json, so the artifact column that would otherwise repeat this table is omitted. Five entries depart from that naming rule. step1_freeze_baseline.py writes baseline_meta.json and baseline.npz; step3_threshold_sensitivity.py writes step3_threshold.json; step12_scenarios.py also writes step12_risk_register.csv; paper_figs.py and appendix_tables.py write into Net3/Figures/paper/; and provenance.py writes cache_manifest.json, which validate_artifacts.py reads without writing an artifact of its own.

One dependency crosses sections and is easy to miss when reproducing a single result. Every displacement reported in baseline posterior standard deviations is divided by the median posterior standard deviation over 30 noise realisations at the baseline noise level, which step6_noise_sensitivity.py writes, and not by the standard deviation of the run being reported.

| Paper section | Script |
| --- | --- |
| 2.2.2, Appendix A | step0_warmup_convergence.py |
| 2.2.4, Appendix B | step13_known_answer.py, step15_unit_equivalence.py |
| 2.3, 3.2.1 | step1_freeze_baseline.py |
| 3.2.2, Appendix C | step3_threshold_sensitivity.py, step4d_displaced_robust.py |
| 2.4.3, 3.3.3, Appendix D | step7_fisher.py |
| 2.4.4, 3.2.3 | step7b_profile.py |
| 2.5.1, 3.3.1, and the standardising denominator for 3.3.2, 3.4 and 3.6.2 | step6_noise_sensitivity.py |
| 2.5.2, 3.3.1 | step7c_ar1.py, step7c_profile_ar1.py |
| 2.5.3, 3.3.2, 3.6.2, Appendix F | step8_sensor_bias.py, step8c_bias_bynode.py, step8d_sensor_drift.py |
| 2.5.5, 3.3.3, 3.6.2 | step8b_kb_sensitivity.py |
| 2.6, 3.4, Appendix E | step5_structural_error.py, step5c_jitter_sweep.py, step5d_structured.py |
| 2.7, 3.5 | step11_loo.py |
| 2.8, 3.6, Appendices G and H | step10_risk_metrics.py, step12_scenarios.py |
| 3.2.3 (repeated-noise calibration) | step14_repeated_noise.py |
| Figures 1 to 7, Tables 1 and 3 to 5 | paper_figs.py |
| Appendix tables | appendix_tables.py |
| Provenance and verification | provenance.py, validate_artifacts.py |