## Slide 1
Weekly
Report
Ruixin Peng
July 17, 2026

## Slide 2
Inverse crime
Truth uses a finer time step (e.g., 60 s WQ step), while calibration uses 300 s.
Truth uses pipe-level heterogeneous kw, while calibration employs grouped parameters. This tests the feasibility of "approximating true heterogeneity with 3 parameters," rather than the circular approach of "recovering 3 parameters using 3 parameters."
Bulk decay is considered perfectly known. (0.4, 0.5, 0.6)

## Slide 3
Parameter | Posterior 5–95% | Median | Prior | True value
kw_old | [-1.456, -0.455] | -0.972 | [-1.5, -0.2] | -1.0
kw_avg | [-0.192, -0.048] | -0.120 | [-0.2, -0.04] | -0.1
kw_new | [-0.095, -0.010] | -0.053 | [-0.10, -0.005] | -0.05
GLUE prior is narrow

## Slide 4
Objective is the global RMSE - Signals from different zones are diluted (wntr_chlorine_getting_started_4)
The threshold-risk metric is a time-averaged measure, which masks the operational reality.
eg. A node that is below the threshold 10% of the time and safe 90% of the time may have the same Pn as another node that is exactly at the threshold edge 100% of the time.